## 1 Preliminaries
SECTION 1
PRELIMINARIES
SPECIAL NOTES
1 | The Contractor is required to check the numbers of the pages and should any be found to be missing or
in duplicate or the figures or writing indistinct, they must inform the Quantity Surveyors at once and have
the same rectified. Should the Contractor be in doubt about the precise meaning of any item, word or
figure, for any reason whatsoever, or observe any apparent omission of words or figures they must inform
the Quantity Surveyor in order that the correct meaning may be decided upon before the date for the
submission of the Tender.
2 | No liability whatever will be admitted nor claim allowed in respect of errors in the Contractor's Tender
due to mistakes in the Bills of Quantities which should have been rectified in the manner described above
3 | Any doubt or obscurity as to the meaning or intention of any part of the tender documents, or any
question arising, shall be taken up in writing, before submission of the tender so that the same can be clarified
4 | The Contractor shall not alter or otherwise qualify the text of these Bills of Quantities. Any alteration
or qualification made without authority will be ignored and the text of the Bills of Quantities as printed will be adhered to.
5 | The Contractor shall be deemed to have made allowance in their prices generally to cover items of
Preliminaries or additions to Prime Cost Sums or other items, if these have not been priced against the respective items
6 | All items of measured work shall be priced in detail and tenders containing lump sums to cover trades or
groups of work must be broken down to show prices for each item before they will be accepted.
Lump sums to cover items of Preliminaries shall likewise be broken down if so required.
7 | In no case will any expenses incurred by Contractors in preparation of this Tender be reimbursed.
8 | The copyright of these Bills of Quantities is vested in the Quantity Surveyors and no part thereof may
be reproduced without their express permission given in writing.
9 | The Contractor is solely responsible for the accurate ordering of materials in accordance with the
Drawings and Architect's instructions and no claims for any loss or expense will be entertained for
orders for materials based upon the Bills of Quantities.
10 | The Bills of Quantities must be priced in US Dollar currency, i.e. US Dollars and Cents.
11 | The tender documents must be priced in ink.
INDEX
| SECTION NO. 1 | PRELIMINARIES AND GENERAL DESCRIPTIONS
| SECTION NO. 2 | MAIN BUILDING
| SECTION NO. 3 | KITCHEN AND DINING
| SECTION NO. 4 | SECURITY OFFICE
| SECTION NO. 5 | MAIN TOILET
| SECTION NO. 6 | SECURITY TOILETS
| SECTION NO. 7 | SECURITY FENCES
| SECTION NO. 8 | WATCH TOWERS
| SECTION NO. 9 | GATES
| SECTION NO. 10 | SEPTIC TANK
| SECTION NO. 11 | GENERATOR HOUSE
| SECTION NO. 12 | WATER STORAGE AND DISTRIBUTION
| SECTION NO. 12 | EXTERNAL WORKS
ITEM | DESCRIPTION
SECTION NO. 1
PRELIMINARIES AND GENERAL DESCRIPTIONS
PRELIMINARY PARTICULARS
1.1 | PARTIES
| The "Employer" is | INTERNATIONAL ORGANIZATION FOR MIGRATION
For the purpose of the works which are under the control of the consultants above, the
respective consultants shall be deemed to be invested with the duties and be representatives
of the Architect.
1.2 | SITE
The site is located in ……………………………………….. DISTRICT
The site of the works shall be used solely for the purpose of executing and completing the
Contract to the satisfaction of the Architect.
The Contractor shall obtain the Architect's approval for the siting of all temporary storage
areas for materials.
The Contractors shall visit the site to acquaint themselves with its nature and position, the
nature of the ground, sub- strata and other local conditions, position of power and water
supplies, access roads or any other limitations, and no claims for extras will be considered
on account of lack of knowledge in this respect.
The Contractor's attention is drawn to the fact that they shall confine themselves to the area
necessary for executing the works as instructed by the Architect.
The contractor must obtain the Architect's approval and directions regarding the use of any
materials found on the Site. Any such material utilized in the execution of the Contract shall be
measured and value assessed by the Quantity Surveyor and the amount credited to the
Employer.
| Carried To Collection | US$
1.3 | GENERAL MATTERS
1.3.1 | SUFFICIENCY OF TENDER
The Contractor shall be deemed to have satisfied themselves before tendering as to the
correctness and sufficiency of their Tender for the Works and of the rates and prices stated
in the priced Bills of Quantities, which rates and prices shall cover all their obligations under the
Contract and all matters and things necessary for the proper completion and maintenance of
the Works.
1.3.2 | STAMP CHARGES
The Contractor shall allow for the payment of all Stamp Charges in connection with the Surety
Bond and Contract Agreement.
1.3.3 | DEFINITIONS AND ABBREVIATIONS
Terms used in these Bills of Quantities shall be interpreted as follows:
| "Approved" | shall mean approved by the Architect.
| "as directed" | shall mean as directed by the Architect or any other consultant in the contract.
| "BS" | Shall mean the current British Standard Specification published by the British
Standards Institution, 2 Park Street, London W.1, England.
| "CM" | shall mean Cubic Meters.
| "SM" | shall mean Square Meters.
| "LM" | shall mean Linear Meters.
| "mm" | shall mean Millimeters.
| "Kg" | shall mean Kilograms.
| "No." | shall mean Number.
| "m.s" | shall mean Measured separately.
| "Ditto " | shall mean as described before or as above described.
1.3.4 | PROGRESS SCHEDULE
The Contractor shall, upon receiving instructions to proceed with the work, draw up a Time
and Progress Schedule setting out the order in which the Works are to be carried out with the
appropriate dates thereof. This Time and Progress Schedule is to be agreed with the Architect
and no deviation from the order set out in this Schedule will be permitted without the written
consent of the Architect. The Main Contractor will be responsible for arranging the above
programme with all Sub-Contractors including the Nominated Sub-Contractors and Nominated
Suppliers.
1.3.5 | FIGURED DIMENSIONS
Figured dimensions are to be followed in preference to dimensions scaled from the Drawings;
but whenever possible dimensions are to be taken on the Site or from the Buildings. Before
any work is commenced by Sub-Contractors or Specialist Firms, dimensions must be checked
on the Site and/or buildings and agreed with the Contractor, irrespective of the comparable
dimensions shown on the Drawings. The Contractor shall be responsible for the accuracy of
such dimensions.
| Carried To Collection | US$
1.3.6 | PROVISIONAL WORK
All "provisional" and other work liable to adjustment under this Contract shall be left uncovered
for a reasonable time to allow all measurements needed for such adjustment to be taken by
the Quantity Surveyor. Immediately the work is ready for measurement, the Contractor shall
give notice to the Quantity Surveyor.
If the Contractor makes default in these respects he shall, if the Architect so directs, uncover
the work at his own expense to enable the measurements to be taken.
1.3.7 | EXISTING SERVICES
Prior to commencement of any work the Contractor is to ascertain from the relevant
Authorities the exact position, depth and level of all existing electric cables, water pipes or
other services in the area and they shall make whatever provisions may be required by the
Authorities concerned for the support and protection of such services. Any damage or
disturbance caused to any services shall be reported immediately to the Architect and the
relevant Authority and shall be made good to their satisfaction at the Contractor's expense.
1.3.7 | TRANSPORT TO AND FROM THE SITE
The Contractor shall include in their prices for the transport of materials, workmen, etc., to and
from the Site of the proposed Works, at such hours and by such routes as are permitted by
the Authorities.
1.3.8 | OVERTIME
The Contractor shall allow in their tender for any extra costs for overtime working they
consider will be necessary in order to complete the works by the contract Date of Completion.
If during the course of the Contract overtime is worked for a specific purpose in accordance
with a written instruction issued by the Architect, the Contractor will be reimbursed in respect
of such overtime to the extent only of the additional net cost of unproductive time payable
over and above the basic hourly rates as laid down by the Regulations of Wages and
Conditions of Employment Act, Building and Construction Industry Wages council and
excluding any bonuses, profits and overheads.
1.3.9 | PUBLIC AND PRIVATE ROADS, PAVEMENTS, ETC.
The Contractor will be required to make good, at their own expense, any damage they may
cause to the present road surfaces and pavements within or beyond the boundary of the Site,
during the period of the Works. In particular, all existing trees, shrubs, plants, etc., which may
be destroyed or damaged during the progress of the Works are to be made good by the
Contractor to the approval of the Architect.
1.3.10 | POLICE REGULATIONS
The Contractor is to allow for complying with all instructions and regulations of the
Police Authorities.
| Carried To Collection | US$
1.4 | CONTRACTORS' SUPERINTENDENCE
The Contractor shall constantly keep on the Works a literate English-speaking Agent or
Representative, competent and experienced in the kind of work involved, who shall give
his whole time to the superintendence of the Works. Such Agent or Representative shall
receive on behalf of the Contractor, directions and instructions from the Architect and such
directions and instructions shall be deemed given to the Contractor in accordance with the
Conditions of Contract. The Agent shall not be replaced without the specific approval of the
Architect.
It is to be a specific condition of this Contract that the successful Tenderer shall provide
on site throughout the period from the completion of the substructure to the Date for
Practical Completion a suitably qualified, experienced and competent person to ensure
that the works are carried out to the standard required by the specification and detailed
on the Drawings; and shall ensure that upon any termination of employment a suitable
replacement is found.
Before the Tenderer's offer is accepted the Architect will personally interview the Contractor's
proposed Representative. A curriculum vitae of past experience and qualifications must be
provided for the Architect's scrutiny.
The Architect's decision will be final regarding the suitability of the proposed Representative.
1.4.1 | WATER
All water shall be fresh, clean and pure, free from earthy vegetable or organic matter, acid or
alkaline substance in solution or suspension.
The Contractor shall provide at their own risk and cost all water for use in connection with the
Works (including the work of Sub-Contractors). The Contractor shall provide at their own
expense all temporary distribution pipes, storage tanks, meters, etc., and they shall clear
away same upon completion of the Works.
1.4.2 | LIGHTING AND POWER
The Contractor shall provide at their own risk and cost all artificial lighting and power for use
on the Works, including all Sub-Contractors' and Specialists' requirements and including all
temporary connections, wiring, fittings, etc., and clearing away on completion. The Contractor
shall pay all fees and obtain all permits in connection therewith.
1.4.3 | SAFETY
In particular there shall be proper provision of planked footways and guard-rails to scaffolding,
etc.; protection against falling materials and tools and the Site shall be kept tidy and clear of
dangerous rubbish.
The Architect shall be empowered to suspend work on the Site should he consider these
conditions are not being observed, and no claim arising from such a suspension will be allowed.
| Carried To Collection | US$
1.4.4 | PROTECTIVE CLOTHING
The Contractor shall provide all protective or any other special clothing or equipment for their
employees that may be necessary.
These shall include, inter-alia, safety helmets, gloves, goggles, earmuffs, gumboots, steel
toed boots, overalls, etc according to the type of work. The Contractor shall ensure
that all safety and protective gear are worn by all staff on site at all times
1.5 | MATERIALS AND WORKMANSHIP
1.5.1 | GENERALLY
All materials shall be new unless otherwise directed or permitted by the Architect and in all
cases where the quality of goods or materials is not described or otherwise specified, is to be
the best quality obtainable in the ordinary meaning of the word "best" and not merely a trade
signification of that word.
All materials and workmanship shall, unless otherwise specified or described, conform to the
appropriate Kenya Bureau of Standards or British Standards Institution Specification current
at the date of tender.
The Contractor shall order all materials to be obtained from overseas immediately after the
Contract is signed and shall also order materials to be obtained from local sources as early as
necessary to ensure that such materials are on Site when required for use in the Works.
The Contractor shall be responsible for and shall replace or make good at their own expense
any materials lost or damaged.
The Works throughout shall be executed by skilled workmen well versed in their respective
trades.
1.5.2 | REJECTED WORKMANSHIP OR MATERIALS
Any workmanship or materials not complying with the specific requirements or approved
samples or which have been damaged, contaminated or have deteriorated, must immediately
be removed from the Site and replaced at the Contractor's expense, as required.
1.5.3 | PROPRIETARY MATERIALS
Where proprietary materials are specified herein-after the Contractor may propose the use of
materials of other manufacture but equal quality for approval by the Architect.
All materials and goods, where specified to be obtained from a particular manufacturer or
supplier are to be used or fixed strictly in accordance with their instructions.
1.5..4 | SAMPLES
The Contractor shall furnish at the earliest possible opportunity before work commences and
at his own cost, any samples of materials or workman-ship that may be called for by the
Architect for his approval or rejection, and any further samples in the case of rejection until
such samples are approved by the Architect and such samples, when approved, shall be the
minimum standard for the work to which they apply.
| Carried To Collection | US$
1.6 | CONCRETE TESTS
Concrete test cubes I.e. per set of three as later described, including testing fees, labour
and materials, making moulds, transport and handling etc.. and ensuing copies of tests
are promptly dispatched to the Architect's and Quantity Surveyor's offices.
Successful tests only (Provisional)
1.7 | TEMPORARY WORKS
1.7.1 | SPACE AND SERVICES FOR THE ARCHITECT
The Contractor shall provide where directed within the site, site offices and clean toilet facilities
for the sole use of the Architect and their representatives to the satisfaction of the Local
Authorities. The offices shall be provided with adequate furniture and the contractor shall
provide the services of a sweeper, pay all charges and keep the facilities in a clean and
sanitary condition during the whole period of the Works. In particular, the Contractor is to
note that the station will continue with operations during the period of the works and a
separate office and store shall be provided for full time use by the station dealer. Equally,
separate sanitary amenities shall be provided for the station staff to the satisfaction of the
Architect and local authorities.
1.7.2 | TELEPHONE
The Contractor shall provide a telephone connection to the town exchange for the period of
the Works, and shall pay all fees and rental for the same. The telephone connection shall
remain on site until completion of the works.
1.7.3 | SANITATION
The Contractor shall make arrangements for the necessary toilet facilities for their staff and
workmen to the requirements and satisfaction of the Health authorities and maintain the same
in a thoroughly clean and sanitary condition and pay all conservancy fees during the period of
the Works and remove when no longer required.
1.7.4 | PLANT, TOOLS AND SCAFFOLDING
The Contractor shall provide all necessary hoists, tackle, plant, vehicles, tools and appliances
of on every description for the due and satisfactory completion of the Works and shall remove
same completion.
The Contractor shall provide, erect and maintain all temporary scaffolding, sufficiently strong
and efficient for the due performance of the Works, including Sub-contract Works, provide
special scaffolding as and when required during the Works and remove on completion and
make good.
Such scaffolding shall be constructed of tubular steel or timber of sufficient scantlings and be
provided with planked footways and guard-rails to approval.
All such plant, tools and scaffolding shall comply with all regulations whether general or local, in
force throughout the period of the Contract and shall be altered or adapted during the Contract
as may be necessary to comply with any amendments in or additions to such regulations.
Scaffolding is not measured hereinafter, and the Contractor must allow here or in his rates for
the above.
| Carried To Collection | US$
1.8 | EXISTING AND ADJACENT PROPERTY
The Contractor must take all steps necessary to safeguard existing and adjacent property,
make good at their own expense any damage to persons or property caused thereon, and
hold the Employer indemnified against any such claim arising.
The Contractor will be held fully responsible for the safety of the existing and adjacent buildings
and for any damage caused in consequence of these Works. They must reinstate all damages
at his own expense and indemnify the Employer against any loss.
The Contractor must take such steps and exercise such care and diligence as to minimize
nuisance from dust, noise or any other cause to the occupiers of the existing and adjacent
property.
1.9 | HOARDING
The Contractor shall enclose the site areas under which work is carried out, with
1.80 meter high barbed wire fence comprising treated blue gum poles at centres not
exceeding 3.0meters and 6No barbed wire strands at equal spacing
The contractors attention is drawn to the fact that some areas of the site are
already built up and shall be in use during the currency of this project. As such
the contractor must allow for keeping his/her employees from interfering with
such other users and preventing and minimizing any nuisance arising from dust,
noise or by way of trespass.
Allow for Provisional length of 100 meters @ (tenderer to insert rate and extend)
1.1 | WATCHING AND LIGHTING
The Contractor shall provide at their risk and cost all watching and lighting as necessary to
safeguard the Works, plant and materials against damage and theft.
1.11 | SIGNBOARD
The Signboard and lettering on same for the display of the General and Sub-Contractors'
names shall be of an approved size with the Employer's name painted thereon. The Architect's
Quantity Surveyor's and other Consultants' names shall be printed in 50 mm letters all to the
Architect's approved design. No other signboard or advertising will be permitted without prior
permission from the Architect.
| Carried To Collection | US$
1.12 | PRIME COST RATES
Where description of items include a P.C. rate per unit this rate is to cover the net supply
cost of the unit only. The Contractor's price must include for the cost of the unit at the rate
stated, plus waste, taking delivery, storage, fixing in position, profit and overheads.
The actual net cost per unit will be adjusted within the Final Account against the P.C. rate
stated.
1.13 | PROTECTION AND CLEANING
1.13.1 | PROTECTION
The Contractor shall cover up and protect from damage, including damage from inclement
weather, all finished work and unfixed materials, including that of Sub-Contractors, etc., to the
satisfaction of the Architect until the completion of the Contract.
1.13.2 | CLEANING
The Contractor shall, upon completion of the Works, at their own expense, remove and clear
away all surplus excavated materials, plant, rubbish and unused materials and shall leave the
whole of the Site and Works in a clean and tidy state to the satisfaction of the Architect,
including clearing away and making good all traces of temporary access roads, offices, sheds,
camps, etc. Particular care shall be taken to leave clean all floors and windows and to remove
all paint and cement stains. They shall also, at the discretion of the Architect, remove all
rubbish and dirt as it accumulates. The Contractor is to find their own dump and shall pay
all charges in connection therewith.
US$
Collection
| Brought forward from Page | 1/4
| Brought forward from Page | 1/5
| Brought forward from Page | 1/6
| Brought forward from Page | 1/7
| Brought forward from Page | 1/8
| Brought forward from Page | 1/9
| Brought forward from Page | 1/10
| Brought forward from Page | 1/11
TOTAL FOR SECTION 1: PRELIMINARIES AND GENERAL DESCRIPTIONS CARRIED TO GRAND SUMMARY
US$

## MAIN BLOCK (hidden)
ITEM | DESCRIPTION | UNIT | Worked Quantities | Comparable Rates | Total
GRANT No. ……………………………………….
PROPOSED ……………………………………....
…….………………………………….. DISTRICT
SECTION 2: MAIN BLOCK
ELEMENT NO. 1 : SITE PREPARATION
A | Clear site of all bushes and debris. Grab up roots and | m2 | 1590 | 3 | 4770
| burn the arisings |  |  |  | 0
0
B | Load, wheel and cart deposit and spread surplus excavated |  |  |  | 0
| material where directed on site at a distance not exceeding |  |  |  | 0
| 100 meters | Item | 1 | 300 | 300
0
| Total carried to summary | $ |  |  | 5070
0
0
0
0
0
| PROPOSED …………………………………….... |  |  |  | 0
| …….………………………………….. DISTRICT |  |  |  | 0
0
| SECTION 2: MAIN BLOCK |  |  |  | 0
0
0
| ELEMENT NO. 2 : SUBSTRUCTURES (PROVISIONAL) |  |  |  | 0
0
0
0
| Excavations including maintaining and supporting sides |  |  |  | 0
| and keeping free from water, mud and fallen material |  |  |  | 0
0
A | Top soil excavation average 200mm deep | m2 | 1425 | 3 | 4275
0
0
B | Excavate trench for foundation not exceeding 1.50 |  |  |  | 0
| meters deep, starting from stripped levels | m3 | 389.7 | 10 | 3897
0
| Ditto |  |  |  | 0
| Column bases | m3 | 67.2 | 10 | 672
0
| Planking and strutting |  |  |  | 0
0
C | Allow for keeping foundations free from water, mud, fallen |  |  |  | 0
| materials, etc. | LS | 500 | 1 | 500
0
| Disposal |  |  |  | 0
0
D | Return, fill and ram selected excavated material around | m3 | 137.07 | 7 | 959.49
E | Load, wheel and cart deposit and spread surplus |  |  |  | 0
| excavated material where directed on site at a |  |  |  | 0
| distance not exceeding 100 meters | m3 | 319.83 | 50 | 15991.5
0
| Hardcore or other approved filling, as described |  |  |  | 0
0
F | 300mm thick well compacted hardcore filling blinded with |  |  |  | 0
| 25mm thick quarry dust layer to receive surface bed | m2 | 1425 | 4 | 5700
0
G | 50mm thick Quarry dust blinding to surfaces of hardcore :rolled | m2 | 1425 | 3 | 4275
| smooth to receive polytheen sheeting (m.s) |  |  |  | 0
0
| Anti-termite treatment |  |  |  | 0
0
H | Gladiator or equal and approved chemical anti-termite |  |  |  | 0
| treatment, executed complete by an approved specialist |  |  |  | 0
| under a ten-year guarantee, to surfaces of blinding | m2 | 1425 | 3 | 4275
0
| Damp-proof membrane |  |  |  | 0
0
I | 1000 gauge polythene or other equal and approved |  |  |  | 0
| damp-proof membrane, laid over blinded hardcore |  |  |  | 0
| (m.s) with 300mm side and end laps (measured |  |  |  | 0
| nett-allow for laps) | m2 | 1425 | 2 | 2850
0
| Reference A142 mesh 200 x 200 mm , weight 2.22 kgs per |  |  |  | 0
| square meter ( measured net - no allowance made for laps |  |  |  | 0
| (inclunding bends, tying wire and distance blocks) |  |  |  | 0
0
J | Fabric ref. A142 weighing 2.22kg/ sq.metre, in surface |  |  |  | 0
| bed | m2 | 1425 | 4 | 5700
0
0
0
| Total carried to summary | $ |  |  | 49094.99
0
0
0
| SECTION 2: MAIN BLOCK |  |  |  | 0
0
| ELEMENT NO. 3 : CONCRETE WORKS |  |  |  | 0
0
| Plain concrete class 15 in: |  |  |  | 0
0
A | 50mm blinding | m2 | 346.4 | 11 | 3810.4
0
| Insitu concrete class 25/20 , vibrated and reinforced as described, in:- |  |  |  | 0
0
| BEAMS |  |  |  | 0
0
A | Ground beam(Strip Footing) | m3 | 103.92 | 220 | 22862.4
0
B | Ring beam 1 | m3 | 77.94 | 220 | 17146.8
0
| COLUMNS |  |  |  | 0
0
A | Columns bases | m3 | 28.8 | 220 | 6336
0
B | Starter columns | m3 | 13.824 | 220 | 3041.28
0
C | Columns (Height 3m) | m3 | 34.56 | 220 | 7603.2
0
| SLABS |  |  |  | 0
0
A | 200mm thick surface bed laid in bays including all |  |  |  | 0
| necessary formwork | m3 | 213.75 | 220 | 47025
0
| Ditto: |  |  |  | 0
0
B | Suspended slab | m3 | 186.6 | 220 | 41052
0
| Reinforcement, as described:-[PROVISIONAL] |  |  |  | 0
0
| High yield square twisted reinforcement bars to B.S 4461 |  |  |  | 0
0
| BEAMS |  |  |  | 0
0
| GROUND BEAM |  |  |  | 0
0
A | Y12 (Nominal Diameter 12mm) bars as main bars, |  |  |  | 0
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 1538.016 | 1.6 | 2460.8256
0
B | R8 (Nominal Diameter 8mm) bars as rings, |  |  |  | 0
| Cross-Sectional Area (50.3mm2), Mass per unit length (0.395kg/m) | Kg | 1202.7798 | 1.6 | 1924.4477
0
| RING BEAM 1 |  |  |  | 0
0
C | Ditto for Y12 as main bars | Kg | 1538.016 | 1.6 | 2460.8256
0
D | Ditto for R8 as rings | Kg | 2138.2752 | 1.6 | 3421.2403
0
| COLUMNS |  |  |  | 0
0
| COLUMN BASES |  |  |  | 0
0
E | Y12 (Nominal Diameter 12mm) bars as main bars, |  |  |  | 0
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 843.9552 | 1.6 | 1350.3283
0
| STARTER COLUMNS |  |  |  | 0
0
F | Y12 (Nominal Diameter 12mm) bars as main bars, |  |  |  | 0
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 537.0624 | 1.6 | 859.2998
0
G | R8 (Nominal Diameter 8mm) bars as rings, |  |  |  | 0
| Cross-Sectional Area (50.3mm2), Mass per unit length (0.395kg/m) | Kg | 404.2584 | 1.6 | 646.8134
0
| COLUMNS |  |  |  | 0
0
| 3m HIGH COLUMNS |  |  |  | 0
0
H | Y12 (Nominal Diameter 12mm) bars as main bars, |  |  |  | 0
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 792.8064 | 1.6 | 1268.4902
0
I | R8 (Nominal Diameter 8mm) bars as rings, |  |  |  | 0
| Cross-Sectional Area (50.3mm2), Mass per unit length (0.395kg/m) | Kg | 1208.3328 | 1.6 | 1933.3325
| SLABS |  |  |  | 0
0
| ROOF SLAB |  |  |  | 0
0
| Y8 (Nominal Diameter 8mm) | Kg | 1811 | 1.6 | 2897.6
| Y10 (Nominal Diameter 10mm) | Kg | 7918 | 1.6 | 12668.8
| Y12 (Nominal Diameter 12mm) bars as main bars bottom 1 | Kg | 1977 | 1.6 | 3163.2
0
| Sawn formwork as described to:- |  |  |  | 0
0
K | To edge of floor slab and steps | m2 | 108 | 4 | 432
0
L | Ditto to sides and soffits of roof slab | m2 | 1764 | 4 | 7056
0
| Total carried to summary | $ |  |  | 191420.2835
0
| SECTION 2: MAIN BLOCK |  |  |  | 0
0
| ELEMENT NO. 4 : WALLING |  |  |  | 0
0
| SUB-STRUCTURE WALLING |  |  |  | 0
0
| Approved compacted hardcore fill bedded and jointed in |  |  |  | 0
| cement sand mortar (1:4) |  |  |  | 0
0
A | 400mm thick rubble stone foundation walling | m2 | 519.6 | 23 | 11950.8
0
| SUPER-STRUCTURE WALLING |  |  |  | 0
0
| 200x400mm hollow block walling bedded and jointed in |  |  |  | 0
| cement and sand (1:4) mortar, reinforcement with and |  |  |  | 0
| including 25mm wide x 20 gauge hoop iron at every |  |  |  | 0
| alternate course as described in: |  |  |  | 0
0
B | 200 mm thick reinforced in every third course | m2 | 1299 | 16 | 20784
0
D | Ditto for dwarf wall | m2 | 46.5 | 16 | 744
0
| Horizontal Damp Proof Course:one layer of 3-ply bituminous felt |  |  |  | 0
| or other equal approved (measured nett-allow for laps) |  |  |  | 0
0
F | 200mm wide; B.S. 743 Type A bitumen hessian base 150 mm laps |  |  |  | 0
| (no allowance made for laps); horizontal, 1 no. layer, bedded in |  |  |  | 0
| cement sand (1:3) mortar | LM | 464 | 3 | 1392
0
G | PCC coping above parapet wall | LM | 33 | 10 | 330
0
H | PCC Vent blocks | m2 | 36 | 8 | 288
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
| Total carried to summary | $ |  |  | 35488.8
0
| SECTION 2: MAIN BLOCK |  |  |  | 0
0
| ELEMENT NO. 5 : ROOF AND ROOF FINISHES |  |  |  | 0
0
ROOF COVERING AND RAINWATER DISPOSAL (GCI Sheet covered area)
(PROVISIONAL)
Roof covering
4.5 | 28 gauge pre painted galvanized corrugated iron sheets on timber structure (ms) | SM | 120 | 2.5 | 300
4.51 | Ridge or hip cap, 28 gauge prepainted | LM | 18 | 0.5 | 9
| Structural Timbers |  |  | -
| SAWN TREATED CYPRESS, Grade S50, pressure |  | 1 | 150 | 150
| impregnated (Provisional) |  | 1 | 50 | 50
4.52 | 100 x 50 mm as trussed rafters, joists and struts | LM | 274 | 1.5 | 411
4.54 | 75x50mm purlins | LM | 186 | 1.5 | 279
4.55 | 50 x 150 mm Hip rafters | LM | 23 | 2.5 | 57.5
4.56 | Ditto, wall plate | LM | 22 | 2.5 | 55
4.57 | 25 x 150mm splice plates | LM | 22 | 1.2 | 26.4
4.58 | 25 x 200mm Ridge board | LM | 12 | 1.5 | 18
| Mild steel |  |  | -
4.59 | 100 × 100 × 100 × 3mm thick angle cleat nailed to timber | NO | 25 | 85 | 2125
| Boarding |  |  | -
| WROT CYPRESS, Prime Grade |  |  | -
4.6 | 25x50mm tongued and grooved boarding to eaves | SM | 14 | 6 | 84
4.61 | 32 x 250 mm Fascia board fixed to rafters | LM | 41 | 5 | 205
| Painting and decorating |  |  | -
4.62 | Knot, prime, stop and apply 3 coats polyurethane varnish to eaves boarding | SM | 14 | 5 | 70
4.63 | Ditto but 3 coats gloss oil paint to fascia board 100-200mm girth | LM | 14 | 5 | 70
| Rainwater disposal |  |  | -
4.64 | 150x150mm 24gauge galvanized mild steel box gutter with galvanized steel brackets at 600mm centers | LM | 18 | 6 | 108
| fixed to fascia board (ms) |  |  | -
4.65 | Ditto, 100mm diameter down pipe fixed with brackets to wall at 1000mm maximum centers | LM | 5 | 2.5 | 12.5
4.66 | Extra over ditto for 600mm swanneck projection | NO | 4 | 5 | 20
4.67 | Ditto shoe | NO | 4 | 5 | 20
4.68 | Knot, prime, stop and apply 3 coats oil paint externally to: |  |  | -
4.69 | Timber fascia 200-300mm girth | LM | 41 | 5 | 205
4.7 | Metal gutter | SM | 0 | 20 | 0
4.71 | Prepare and apply bituminous paint to inside of gutter | SM | 0 | 5 | 0
| ROOF STRUCTURE (CONCRETE FLAT ROOF AREA) |  |  |  | 0
0
| Prepare and apply APP high performance waterproofing |  |  |  | 0
| membrane obtained from an approved manufacturer and |  |  |  | 0
| applied according to the manufacturer's instructions |  |  |  | 0
0
A | 4mm APP membrane applied to roof slabs including screeding | m2 | 933 | 15 | 13995
0
B | Dress membrane round 100mm rainwater outlet (provisional) | No. | 20 | 10 | 200
0
| Lightweight water proofed screeds and plaster |  |  |  | 0
0
C | 30mm average plaster gutter walls | SM | 40 | 5 | 200
0
D | 50mm average screed laid to falls and cross falls to | SM | 933 | 5 | 4665
| gutter slabs |  |  |  | 0
0
E | 50x50mm triangular fillet | LM | 140 | 5 | 700
0
| Rain water goods |  |  |  | 0
0
F | Allow for 100mm dia. Fulbora outlet including 100mm heavy duty PVC pipe |  |  |  | 0
| as storm water drainage | No. | 30 | 8 | 240
0
G | Allow for GI stair fixed to wall to access roof | No. | 1 | 120 | 120
0
| ROOF AND ROOF FININSHES CARRIED TO SUMMARY |  |  |  | 24395.4
| Floor Finishes |  |  |  | 0
0
| Cement and sand (1:3) screeds, backings, beds etc |  |  |  | 0
0
A | 25mm Thick cement/sand (1:4) screed to receive Ceramic |  |  |  | 0
| floor tiles (measured separately) | m2 | 1425 | 4 | 5700
0
| Lightweight water proofed screeds and plaster |  |  |  | 0
0
| Rustic 300x300mm ceramic Tiles from approved supplier fixed |  |  |  | 0
| with 'seal master 101' or equal and approved tile adhesive: |  |  |  | 0
| jointed and pointed in 'seal master 201' grout: clean with |  |  |  | 0
| approved detergent and apply 'Johnson wax' polish: allow for |  |  |  | 0
| tile spacers: on |  |  |  | 0
0
C | Floor tiles | m2 | 1425 | 13 | 18525
0
D | Skirtings; |  |  |  | 0
| 100mm wide with rounded junction with wall finish and coved junction |  |  |  | 0
| with floor finish | m2 | 67 | 13 | 871
0
0
E | Ditto for edge of steps and slab | m2 | 29.4 | 13 | 382.2
0
| Wall Finish |  |  |  | 0
0
| 15 mm cement and sand (1:3) render, finished with |  |  |  | 0
| woodfloat to:- |  |  |  | 0
0
F | Concrete or masonry surfaces internally and externally |  |  |  | 0
| Painting | m2 | 2598 | 3 | 7794
0
| Fill uneven surfaces with stucco filler to approval and apply |  |  |  | 0
| two coats soft white external textured paint to: |  |  |  | 0
0
G | Plastered and rendered surfaces | m2 | 2598 | 3 | 7794
0
| Prepare and apply two undercoats of brilliant white emulsion paint |  |  |  | 0
| (RAL Code 9001) and two finishing coats of first quality brilliant white |  |  |  | 0
| Silk Vinyl emulsion paint (RAL Code 9001) to;- |  |  |  | 0
0
H | Plastered surfaces internally and externally | m2 | 2598 | 3 | 7794
0
I | Ditto to soffits of suspended slabs | m2 | 1038 | 3 | 3114
0
0
0
0
| Total carried to summary | $ |  |  | 51974.2
0
| SECTION 2: MAIN BLOCK |  |  |  | 0
0
| ELEMENT NO. 7 : ELECTRICAL INSTALLATIONS |  |  |  | 0
0
| Lighting Fittings |  |  |  | 0
0
| Supply and install following lighting fixtures with all accessories |  |  |  | 0
| as per the specifications and drawings and complete with lamp |  |  |  | 0
| fitting and accessories of Engineer or approved make. |  |  |  | 0
0
A | Type 4S - 4x18w surface mount flourescent light fitting as |  |  |  | 0
| Phillips or equivalent | No. | 42 | 20 | 840
B | Type 4S - 2x18w surface mount flourescent light fitting
| Phillips or equivalent | No. | 14 | 20 | 280
C | Type W1 - 1x36w Surface mounted waterproof polycarbonate
| flourescent light fitting | No. | 8 | 30 | 240
D | 150W LED floodlight | No. | 4 | 50 | 200
Switches
E | 5 Amps one gang one way switch | No | 24 | 10 | 240
F | 5 Amps two gang one way switch | No | 8 | 10 | 80
0
| Socket outlets |  |  |  | 0
0
| Supply and installation of fused shuttered switched socket outlet |  |  |  | 0
| to comply with relevant BS standard (Clipsal, Orange, Crabtree/ |  |  |  | 0
| Tenby/ABB or equivalent). Wiring (including supply of earth wire |  |  |  | 0
| and all other material required) of above socket outlet using approved |  |  |  | 0
| type 2.5mm² PVC/PVC copper cable and 2.5mm² earth wire drawn |  |  |  | 0
| through securely fixed concealed PVC conduit in a ring circuit. |  |  |  | 0
| Socket outlet points |  |  |  | 0
G | 13 A twin sockets outlet | No | 72 | 15 | 1080
Cables, Cable pathways and Conduits
Supply, install, test and commission 450/750 volts 6491X cables with
all required accessories for proper installation and operation including
conduits, pipes( each cable in separate conduit or pipe), cable lugs,
ties... etc. as shown on drawing, as per the preamble, the specifications
and supervision engineer's requirements.
H | Supply, install and connect complete 1.5 sq. mm colour-coded SC
cables to lighting points drawn in Concealed /surface 20mm HG PVC
conduits, complete with draw boxes, switch boxes and other necessary
| accessories. | M | 400 | 8 | 3200
I | Supply and install two compartment floor recessed metallic electrical
floor box with flap cover complete with lifting handle, cable cable flaps,
| as Crabtree Britmac or equal and approved | No. | 1 | 30 | 30
J | Allow for structured cabling with network points as described neatly
| concealed in 4x2" metal trunking | LS | 1 | 2000 | 2000
HVAC
K | Supply, Deliver, Install, Test and Commission the following AC indoor units
including with all accessories including all connections as described.
Wall mounted unit of cooling capacity: 12.3kW with inbuilt drain pump,
power input: 0.15kW, single phase, Refrigerant R-410A complete with all hanging
accessories, remote control, filter chamber, drain pump kit, suction canvas, ceiling
panel, wiring from DP switch to fan coil unit, fabricated steel mounting brackets,
steel frames and raw bolts, anti-vibration mountings. DP switch to be positioned
next to the in door unit. The indoor unit shall be to Daikin/Toshiba/LG make or
| approved equivalent. | No. | 24 | 500 | 12000
| Total carried to summary | $ |  |  | 20190
SECTION 2: MAIN BLOCK
ELEMENT NO. 8 : PLUMBING INSTALLATIONS
PIPING
Supply, deliver and install pipes, tubing and fittings as described and
shown on the drawings. The pipes shall be PPR PN 20 pipes and all
conforming to the current European standards for PPR installations and
to the Engineers approval, pipe jointing shall be by polyfusion or use of
electric coupling and to manufacturer's printed instructions. Rates must
allow for all Metal/plastic threaded adaptors where required, valves,
unions, sockets, sliding and fixed joints, support raceways, isolating
sheaths, elastic material, expansion arms and bends, crossovers, couplings,
clippings, connectors, joints and for the connection of sanitary fixtures etc.
as required in the running lengths of pipework and also where necessary,
for pipe fixing clips, holder bats plugged and screwed for the proper and
satisfactory functioning of the system. The pipes will be pressure tested
before the plastering of wall commences and as per the manufacturers
recommended testing procedures. The sizes indicated are the minimum
bore sizes.
A | Supply and install heavy duty PPR pipes including all connections | LS | 1 | 700 | 700
SANITARY INSTALLATIONS
Sanitary appliances complete with all the connections to services,
waste, jointing to supply overflows and plugging and scewing
to the floors. Where trade names are mentioned below, the
reference is intended to be as a guide to the type of fitting.
B | Pedestal wash hand basin in white vitreous china size 500x400 mm
complete with 'Aztec' chromed taps and handles, a 32mm diameter
chrome plated pop-up waste and a 32mm Caradon Terrain' plastic
bottle trap. Wash hand basin to be as 'Twyford Galerie Design' or equal
| and approved | No. | 2 | 80 | 160
C | Water closet (W.C.) suite in white vitreous china comprising:
Glazed W.C. pan with heavy duty unbreakable plastic seat and cover,
close couple cistern and fittings, 6.0 litres, including chrome lever and
cover clip and WC outlet connector. The cistern to have internal overflow.
| Water closet pan to be as 'Twyford classic' or equal and approved | No. | 4 | 80 | 320
D | Recessed toilet roll holder in white vitreous china size 150x150 mm.
| To be as 'Twyford' or equal and approved | No. | 4 | 15 | 60
E | Wall-mounted push-button soap dispenser complete with initial charge
and mounting brackets. Soap dispenser to be as 'Star mix' or equal
| and approved | No. | 2 | 20 | 40
F | 6 mm thick polished beveled plate glass mirror size 610x610 mm on
foam and 6 mm plywood timber backing in hard wood timber framing
| fixed on wall with dome headed brass screws | No. | 2 | 10 | 20
H | Allow for all all connections, pressure testing at 4 bars for 24hours and
commissioning of the sanitary fittings and accessories to the entire
| satisfaction of the Engineer. | LS | 1 | 200 | 200
0
0
0
| Total carried to summary | $ |  |  | 1500
| SECTION 2: MAIN BLOCK |  |  |  | 0
0
| ELEMENT NO. 9 : OPENINGS |  |  |  | 0
0
| WINDOWS |  |  |  | 0
0
| Extruded anodised aluminium sliding frame 80x50mm mosquito |  |  |  | 0
| netting and fabricated aluminium burglar proof grill with 6mm thick |  |  |  | 0
| glass with blue anti-glare film. |  |  |  | 0
0
A | Overall size 800 x 600mm high | No. | 4 | 60 | 240
0
B | Overall size 1500 x1200mm high | No. | 57 | 150 | 8550
0
C | Overall size 1200 x 1200mm high | No. |  | 120 | 0
0
D | Precast concrete window cill size 260 x 50mm Thick sunk - weathered |  |  |  | 0
| and throated and bedded and jointed in cement sand mortar | No. | 61 | 20 | 1220
0
| DOORS |  |  |  | 0
0
| 45mm thick solid core flush door to B.S 459: parts faced both |  |  |  | 0
| sides with 6mm mahogany veneered plywood and lipped on |  |  |  | 0
| all edges in hardwood, including all planted moulding. |  |  |  | 0
| Complete with heavy duty hinges, brass locks and glass ventilight |  |  |  | 0
0
0
A | 50mm thick single door overall size 900x2400mm high | No. | 27 | 250 | 6750
0
B | 50mm thick double door overall size 1200x2400mm high | No. | 9 | 300 | 2700
0
| IRONMONGERY |  |  |  | 0
0
| Supply delivery and fix the following ironmongery |  |  |  | 0
| with matching screws |  |  |  | 0
0
C | 100mm heavy duty butt hinges | Pairs | 40.5 | 8 | 324
0
D | Ditto: Double door | Pairs | 18 | 10 | 180
0
F | 3 lever mortice lock as Union 2277complete with |  |  |  | 0
| Union 2277 683 -06 -2 brass lever furniture | No. | 27 | 40 | 1080
0
G | Ditto: Double door | No. | 9 | 40 | 360
0
0
0
0
0
0
0
0
0
0
0
0
| Total carried to summary | $ |  |  | 21404
MAIN SUMMARY
No.
| 1 |  |  |  | 5070
| 2 |  |  |  | 49094.99
| 3 |  |  |  | 191420.2835
| 4 |  |  |  | 35488.8
| 5 |  |  |  | 24395.4
| 6 |  |  |  | 51974.2
| 7 |  |  |  | 20190
| 8 |  |  |  | 1500
| 9 |  |  |  | 21404
| Grand Total |  |  |  | 400537.6735
| TOTAL FOR SECTION 5: CARRIED TO GRAND SUMMARY |  |  |  | 400537.6735

## 2 MAIN BUILDING 1
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL
PROPOSED ……………………………………....
SECTION 2: FLAT PACK MODULES
2 | 7 No. FLAT PACK MODULES 12.4 X 6.5M EACH, including Dining hall
2.1 | ELEMENT NO. 1 : SUB-STRUCTURES (all provisional)
2.1 | Clear site of all bushes and debris. Grab up roots and | m2 | 1200 |  | 0
| burn the arisings |  |  |  | 0
0
2.2 | Excavate over site 200 mm deep to remove vegetable soil and cart away to spoil heap where directed on site | m2 | 1200 |  | 0
0
Hardcore or other approved filling, as described
2.3 | 300mm thick approved hardcore filling compacted and laid in layers not exceeding 150 mm thick | m2 | 950 |  | 0
0
2.4 | 50mm thick Quarry dust blinding to surfaces of hardcore :rolled smooth to receive polytheen sheeting (m.s) | m2 | 950 |  | 0
| Anti-termite treatment |  |  |  | 0
0
| Gladiator or equal and approved chemical anti-termite |  |  |  | 0
| treatment, executed complete by an approved specialist |  |  |  | 0
2.5 | under a ten-year guarantee, to surfaces of blinding | m2 | 950 |  | 0
0
| Damp-proof membrane |  |  |  | 0
0
| 1000 gauge polythene or other equal and approved | m2 | 950 |  | 0
2.6 | damp-proof membrane, laid over blinded hardcore |  |  |  | 0
| (m.s) with 300mm side and end laps (measured |  |  |  | 0
| nett-allow for laps) |  |  |  | 0
0
| Formwork |  |  |  | 0
0
2.7 | To the edges of ground slabs 100 - 200mm wide | lm | 304 |  | 0
0
| Reinforcement |  |  |  | 0
0
2.8 | Mesh reinforcement reference A142 weighing 2.22kg/m2 in ground slabs | m2 | 950 |  | 0
0
Concrete Works
| Insitu concrete class 25/20 , vibrated and reinforced as described, in:- |  |  |  | 0
0
2.9 | 150 mm Ground floor slab | SM | 950 |  | 0
0
Floor Finish
| Cement and sand (1:3) screeds |  |  |  | 0
0
2.1 | 25mm Thick cement/sand (1:4) screed steel trowelled | SM | 950 |  | 0
Page Total Carried Forward
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL
Page Total Brought Forward
SUPER STRUCTURE
ELEMENT NO. 2: PREFABRICATED PANELS
2.11 | Attendance to the contractor fixing prefabricated panels supplied by IOM and fixed to the manufacturers specification and details. The panels will be placed on top of the concrete slab | Item | Sum |  | 0
ELEMENT NO. 3: ELECTRICAL WORKS
2.12 | Connection to the existing electrical supply system | Item | Sum
Note: All the above units come complete with wiring and electrical fittings and the contrcator is required to plug in to the power supply system and test the units.
ELEMENT NO. 4: STEPS AND RUMPS
2.13 | Construct to specification steps and rumps as indicated on the drawing | Item | Sum
ELEMENT NO. WASH AREA FOR PRAYERS
2.14 | Construct 1 No continous concrete bench consisting of 400x2000x100mm thick reinforced concrete slab with T8 @ 200mm C/C on double 200mm thick by 400mm high block wall with an extra 400mm bellow the ground . Construct also 800mm high by 200mm thick by 2000mm long block wall for the support of plumbing and water tap. Fill the area between the wall and the bench with hardcore and 100mm thick reinforced concrete slab with T8 200mm C/C 2000mm long at the top and steel trowel to a smooth finish. Fix 3No. taps to specification. Tile all areas in contact with water including the bench. | Item | Sum
ELEMENT NO. WASH HAND AREA FOR THE DINING
2.15 | Allow for external ablution area outside the dining for washing hands. This will consist of reinforced of construction of 1200mm high by 200mm thick by 1000mm long block wall for the support of plumbing and water tap. A 100mm thick reinforced concrete slab with T8 200mm C/C 1000mm long at the top and 600mm side, steel trowel to a smooth finish. Fix 3No. taps to specification. Tile all areas in contact with water including the bench. | Item | Sum
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL
PAGE TOTAL BROUGHT FORWARD
ELEMENT 2 : SOAK PIT 2 No. (For both Ablution areas)
11.19 | Excavate 1.5m diameter x 3.5m depth pit each | C.M | 11 |  | 0
11.2 | Backfill with well packed approved hardcore to 2m depth | C.M | 7 |  | 0
11.21 | Plastic sheeting | S.M | 4 |  | 0
11.22 | 200mm thick normal soil backfill | C.M | 1 |  | 0
TOTAL CARRIED TO GRAND SUMMARY

## 3 Kitchen
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL
GRANT No. ……………………………………….
PROPOSED ……………………………………....
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL
3 | SECTION 3: KITCHEN
3.1 | ELEMENT NO. 1 : SUB-STRUCTURES (all provisional)
3.1.1 | Clear site of all bushes and debris. Grab up roots and | sm | 54 |  | 0
| burn the arisings |  |  |  | 0
0
3.1.2 | Excavate over site 200 mm deep to remove vegetable soil and cart away to spoil heap where directed on site | sm | 54 |  | 0
0
3.1.3 | Excavate trench for foundation trenches and column bases not exceeding 1.50 meters deep, starting from stripped levels | cm | 40 |  | 0
0
3.1.4 | Fill trenches with hard core compacted in 150 mm layers | cm | 20 |  | 0
0
3.1.5 | 50mm thick Quarry dust blinding to surfaces of hardcore :rolled smooth to receive polytheen sheeting (m.s) | sm | 54 |  | 0
0
3.1.6 | Return fill in and ram selected excavated material around foundations | cm | 12 |  | 0
3.1.7 | Spread surplus excavated material on site as directed | cm | 8 |  | 0
0
3.1.8 | Allow for keeping foundations free from water, mud, fallen | Item | Sum |  | 0
materials, etc.
0
3.1.9 | Allow for planking and strutting as necessary to sides of excavation | Item | Sum |  | 0
0
| Concrete Works |  |  |  | 0
| Plain concrete class 15 in: |  |  |  | 0
0
3.1.10 | 50mm blinding | sm | 30 |  | 0
0
| Insitu concrete class 25/20 , vibrated and reinforced as described, in:- |  |  |  | 0
0
3.1.11 | Foundation Strip | cm | 7.5 |  | 0
0
3.1.13 | 150 mm Ground floor slab | sm | 54 |  | 0
0
| Page Total Carried Forward to Next Page |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QTY |  | TOTAL
Total Brought Forward from Previous Page
| Formwork |  |  |  | 0
0
3.1.15 | To the edges of ground slabs 100 - 200mm wide | lm | 42 |  | 0
0
| Reinforcement |  |  |  | 0
0
| High Tensile mild steel reinforcement bars to BS 8666 in Foundations |  |  |  | 0
0
3.1.17 | 10 mm diameter | kg | 80 |  | 0
0
3.1.19 | Mesh reinforcement reference A142 weighing 2.22kg/m2 in ground slabs | m2 | 54 |  | 0
0
| Walling for foundation |  |  |  | 0
3.1.22 | 400mm thick rubble stone foundation walling | m2 | 15 |  | 0
0
| Filling |  |  |  | 0
3.1.23 | 300mm thick approved hardcore filling compacted and laid in layers not exceeding 150 mm thick | m2 | 54 |  | 0
0
3.1.24 | 50mm thick Quarry dust blinding to surfaces of hardcore :rolled smooth to receive polytheen sheeting (m.s) | m2 | 54 |  | 0
| Anti-termite treatment |  |  |  | 0
0
3.1.20 | Gladiator or equal and approved chemical anti-termite |  |  |  | 0
| treatment, executed complete by an approved specialist |  |  |  | 0
| under a ten-year guarantee, to surfaces of blinding | m2 | 54 |  | 0
0
| Damp-proof membrane |  |  |  | 0
0
3.1.21 | 1000 gauge polythene or other equal and approved | m2 | 54 |  | 0
| damp-proof membrane, laid over blinded hardcore |  |  |  | 0
| (m.s) with 300mm side and end laps (measured |  |  |  | 0
| nett-allow for laps) |  |  |  | 0
0
| PAGE TOTAL CARRIED FORWARD |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QTY |  | TOTAL
| PAGE TOTAL BROUGHT FORWARD |  |  |  | 0
| SUPER STRUCTURE |  |  |  | 0
0
3.2 | ELEMENT NO. 2: REINFORCED CONCRETE |  |  |  | 0
0
3.2.1 | Reinforced concrete class 25 in |  |  |  | 0
0
3.2.3 | Beams | m3 | 10 |  | 0
0
| Formwork |  |  |  | 0
0
3.2.4 | To sides and soffits of beams | m2 | 50 |  | 0
0
| Reinforcement |  |  |  | 0
0
| High Tensile mild steel reinforcement bars to BS 8666 in Foundations |  |  |  | 0
0
3.2.5 | 12 mm diameter | Kg | 60 |  | 0
0
| ELEMENT NO. 3: WALLING |  |  |  | 0
3.2.6 | 200mm precast concrete concrete block walls bedded and jointed in cement and sand (1:4) mortar | sm | 18 |  | 0
0
| Horizontal Damp Proof Course:one layer of 3-ply bituminous feltor other equal approved (measured nett-allow for laps) ; B.S. 743 Type A bitumen hessian base 150 mm laps (no allowance made for laps); horizontal, 1 no. layer, bedded in cement sand (1:3) mortar |  |  |  | 0
0
3.2.6 | 200mm wide | LM | 52 |  | 0
0
3.3 | ELEMENT NO. 4 : ROOFING |  |  |  | 0
| ROOF COVERING AND RAINWATER DISPOSAL |  |  |  | -
-
| Roof covering |  |  |  | -
3.2.1 | 28 gauge pre painted IT4 box profile iron sheets on timber structure (ms) | SM | 66 |  | 0
3.2.2 | Ridge or hip cap, 28 gauge prepainted | LM | 6 |  | 0
Structural Timbers
SAWN TREATED CYPRESS, Grade S50, pressure
impregnated
3.2.3 | 100 x 50 mm as trusses and rafters | LM | 50 |  | 0
3.2.4 | 50 x 50 mm as trusses, trussed joists and struts | LM | 92 |  | 0
3.2.5 | 75x50mm purlins and joists and struts | LM | 60 |  | 0
3.2.6 | 100 x 50 mm as King post | LM | 6 |  | 0
3.2.7 | Ditto, wall plate | LM | 42 |  | 0
| PAGE TOTAL CARRIED FORWARD |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL
| PAGE TOTAL BROUGHT FORWARD |  |  |  | 0
3.2.8 | 25 x 200mm Ridge board | LM | 6 |  | 0
| Dittob but for Fascia Board | LM | 12 |  | 0
Rainwater disposal
3.2.9 | 150x150mm 24gauge galvanized mild steel box gutter with galvanized steel brackets at 600mm centers fixed to fascia board (ms) | LM | 12 |  | 0
3.2.10 | Ditto, 100mm diameter down pipe fixed with brackets to wall at 1000mm maximum centers | LM | 4 |  | 0
3.2.11 | Extra over ditto for 600mm swanneck projection | NO | 4 |  | 0
3.2.12 | Ditto shoe | NO | 4 |  | 0
3.2.13 | Knot, prime, stop and apply 3 coats oil paint externally to:
3.2.14 | Timber fascia 200-300mm girth | LM | 12 |  | 0
3.2.15 | Metal gutter | LM | 12 |  | 0
0
3.3 | ELEMENT NO. 5 : WINDOWS
Extruded anodised aluminium sliding frame 80x50mm mosquito netting and fabricated aluminium burglar proof grill with 6mm thick glass with blue anti-glare film.
3.3.1 | Overall size 1500 x1500mm high | No. | 7 |  | 0
0
| Overall size 2000 x1500mm high | No. | 2 |  | 0
0
3.3.2 | Precast concrete window cill size 260 x 50mm Thick sunk - weathered and throated and bedded and jointed in cement sand mortar | lm | 15 |  | 0
3.4 | ELEMENT NO. 6: DOORS
Internal Doors
3.4.1 | 45 mm thick solid steel panelled double door overall size 1200mm * 2400mm high with and including 150*50 mm steel frame, 3 pairs heavy duty brass butt hinges and 5 lever UNION ribitted door lock | No. | 1 |  | 0
0
| External Doors |  |  |  | 0
3.4.2 | 45 mm thick solid steel panelled double door overall size 1200mm * 2400mm high with and including 150*50 mm steel frame, 3 pairs heavy duty brass butt hinges and 5 lever UNION ribitted door lock | No. | 2 |  | 0
0
| PAGE TOTAL CARRIED FORWARD | $ |  |  | 0
ITEM | DESCRIPTION | UNIT | QTY |  | TOTAL
| PAGE TOTAL BROUGHT FORWARD |  |  |  | 0
3.5 | ELEMENT NO. 7 : FINISHES |  |  |  | 0
| Floor Finishes |  |  |  | 0
| Cement and sand (1:3) screeds, backings, beds etc |  |  |  | 0
3.5.1 | 25mm Thick cement/sand (1:4) screed to receive Ceramic |  |  |  | 0
| floor tiles (measured separately) | SM | 54 |  | 0
| Lightweight water proofed screeds and plaster |  |  |  | 0
| Non-slip 300x300mm ceramic Tiles from approved supplier fixed |  |  |  | 0
| with approved tile adhesive: |  |  |  | 0
| jointed and pointed in approved grout. |  |  |  | 0
3.5.2 | Floor tiles | m2 | 54 |  | 0
0
| Skirtings; |  |  |  | 0
3.5.3 | 100mm wide with rounded junction with wall finish and coved junction with floor finish | lm | 42 |  | 0
0
| Wall Finish |  |  |  | 0
| Plastered surfaces |  |  |  | 0
3.5.4 | Internal Lime Plaster | sm | 160 |  | 0
0
3.5.5 | 15 mm cement and sand (1:3) External cement sand rendering | sm | 160 |  | 0
0
| Glazed tiles |  |  |  | 0
3.5.6 | 6 mm glazed wall tiles fixed to plastered surfaces with approved adhesive to a height of 1200 mm in kitchen areas above counter top | sm | 84 |  | 0
0
| Painting |  |  |  | 0
| Fill uneven surfaces with stucco filler to approval and apply two coats soft white external textured paint to: |  |  |  | 0
0
3.5.7 | Plastered and rendered surfaces | sm | 236 |  | 0
| Prepare and apply two undercoats of brilliant white emulsion paint |  |  |  | 0
| (RAL Code 9001) and two finishing coats of first quality brilliant white |  |  |  | 0
| Silk Vinyl emulsion paint (RAL Code 9001) to;- |  |  |  | 0
0
3.5.8 | Plastered surfaces internally and externally | sm | 236 |  | 0
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL
PAGE TOTAL BROUGHT FORWARD
KITCHEN CABINETS
3.9 | Work tops and Bottom Cabinets
3.9.1 | Construct 200mm thick 800mm high massonry walls forkitchen platfor support | SM | 4.8 |  | 0
3.9.2 | Concrete class 20 in 50mm thick plinth and work top | SM | 12 |  | 0
3.9.3 | No. A 142 Fabric mesh reinforcement weighing 2.22 kg per metre square fixed in slab | SM | 12 |  | 0
3.9.4 | Formwork to of slab | SM | 12 |  | 0
3.9.5 | Formwork to edge of slab. 50mm high | LM | 50 |  | 0
3.9.6 | Plaster to soffit of slab and bottom | SM | 12
3.9.7 | Ceramic tiles to worktop including screed | SM | 12
3.9.8 | Veneered mahogany 20mm thick in cupboard doors, divisions and shelves | SM | 16
3.9.9 | Malpa Hinges | Pairs | 25
3.9.10 | Allow for fitting sink to worktop | Item | Sum
3.9.11 | Supply and apply three coats of gloss paint as finish | SM
| Total: Work tops and Bottom Cabinets |  | 16
Over head Cabinets
3.9.12 | MDF for bearers, support cupboard doors and division and shelves nailed and hang as per the drawings | SM | 30
3.9.13 | Supply and fix malpa hinges | Pairs | 15
3.9.14 | Supply and apply three coats of gloss paint as finish | SM | 30
3.9.15 | Total: Over head Cabinets
Plumbing Fittings
Kitchen sink
3.9.16 | Supply and Install double bowl double drainer stainless steel kitchen sink size 1200 x 1200 with EACH bowl size 400 x 340 x 150mm complete with 1 No. Bricon kitchen mixer and tap 40mm waste outlet chain and plug, overflow, 40mmtubular 'P' trap No. WF 8491XX and all required plumbing connections. Sink to be as "ASL"or equal and approved. The sink to be in heavy duty sheet. | NO | 2
Total: Plumbing Fittings
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | RATE
PAGE TOTAL BROUGHT FORWARD
3.1 | ELEMENT NO. 8 : PLUMBING INSTALLATIONS
PIPING
Supply, deliver and install pipes, tubing and fittings as described and shown on the drawings. The pipes shall be PPR PN 20 pipes and all conforming to the current European standards for PPR installations and o the Engineers approval, pipe jointing shall be by polyfusion or use of electric coupling and to manufacturer's printed instructions. Rates must allow for all Metal/plastic threaded adaptors where required, valves, unions, sockets, sliding and fixed joints, support raceways, isolating sheaths, elastic material, expansion arms and bends, crossovers, couplings,clippings, connectors, joints and for the connection of sanitary fixtures etc.as required in the running lengths of pipework and also where necessary, for pipe fixing clips, holder bats plugged and screwed for the proper and satisfactory functioning of the system. The pipes will be pressure tested before the plastering of wall commences and as per the manufacturers recommended testing procedures. The sizes indicated are the minimum bore sizes.
3.10.1 | Supply and install heavy duty PPR pipes including all connections | LS | 1
3.11 | Fire Fighting Services
Supply and Install
3.11.1 | 4.5 Litres discharge controlled type carbon dioxide gas portable fire extinguisher manufactured to BS 5423 with normal charge | NO | 2
3.11.2 | 9Kg dry powder multi-purposed fire class A, B and C as manufactured by Angus Fire Armour ABC multipurpose model AP 9K or equal and approved | NO | 2
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY |  | TOTAL
| PAGE TOTAL BROUGHT FORWARD |  |  |  | 0
3.12 | ELEMENT NO. 7 : ELECTRICAL INSTALLATIONS |  |  |  | 0
0
| Lighting Fittings |  |  |  | 0
0
| Supply and install following lighting fixtures with all accessories |  |  |  | 0
| as per the specifications and drawings and complete with lamp |  |  |  | 0
| fitting and accessories of Engineer or approved make. |  |  |  | 0
0
3.12.1 | Type 4S - 4x18w surface mount flourescent light fitting as |  |  |  | 0
| Phillips or equivalent | No. | 2 |  | 0
3.12.2 | Type W1 - 1x36w Surface mounted waterproof polycarbonate flourescent light fitting | No. | 8 |  | 0
3.12.3 | 150W LED floodlight | No. | 4 |  | 0
Switches
3.12.4 | 5 Amps one gang one way switch | No | 2 |  | 0
3.12.5 | 5 Amps two gang one way switch | No | 2 |  | 0
0
| Socket outlets |  |  |  | 0
0
| Supply and installation of fused shuttered switched socket outlet to comply with relevant BS standard (Clipsal, Orange, Crabtree/ Tenby/ABB or equivalent). Wiring (including supply of earth wire and all ther material required) of above socket outlet using approved type 2.5mm² PVC/PVC copper cable and 2.5mm² earth wire drawn through securely fixed concealed PVC conduit in a ring circuit |  |  |  | 0
| Socket outlet points |  |  |  | 0
3.12.6 | 13 A twin sockets outlet | No | 6 |  | 0
| Page Total Carried to Forward |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QTY |  | TOTAL
| Page Total Brought Forward |  |  |  | 0
Cables, Cable pathways and Conduits
Supply, install, test and commission 450/750 volts 6491X cables with all required accessories for proper installation and operation including conduits, pipes( each cable in separate conduit or pipe), cable lugs, ties... etc. as shown on drawing, as per the preamble, the specifications and supervision engineer's requirements.
3.12.7 | Supply, install and connect complete 1.5 sq. mm colour-coded SC cables to lighting points drawn in Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | M | 55
Supply and install two compartment floor recessed metallic electrical
floor box with flap cover complete with lifting handle, cable cable flaps,
3.12.8 | as Crabtree Britmac or equal and approved | No. | 1 |  | 0
Allow for structured cabling with network points as described neatly
3.12.9 | concealed in 4x2" metal trunking | LS | 1 |  | 0
HVAC
Supply, Deliver, Install, Test and Commission the following AC indoor units
including with all accessories including all connections as described.
Wall mounted unit of cooling capacity: 12.3kW with inbuilt drain pump,
power input: 0.15kW, single phase, Refrigerant R-410A complete with all hanging
accessories, remote control, filter chamber, drain pump kit, suction canvas, ceiling
panel, wiring from DP switch to fan coil unit, fabricated steel mounting brackets,
steel frames and raw bolts, anti-vibration mountings. DP switch to be positioned
next to the in door unit. The indoor unit shall be to Daikin/Toshiba/LG make or
3.12.10 | approved equivalent. | No. | 1 |  | 0
0
TOTAL CARRIED TO GRAND SUMMARY

## Sheet1 (hidden)
| ROOF COVERING AND RAINWATER DISPOSAL |  |  | - | -
| (PROVISIONAL) |  |  | - | -
| Roof covering |  |  | - | -
4.5 | 28 gauge pre painted galvanized corrugated iron sheets on timber structure (ms) | SM | 1134 | 2.5 | 2835
4.51 | Ridge or hip cap, 28 gauge prepainted | LM | 134 | 0.5 | 67
| Structural Timbers |  |  | -
SAWN TREATED CYPRESS, Grade S50, pressure
impregnated (Provisional)
4.52 | 150 x 50 mm as trusses | LM | 935.97 | 2.5 | 2339.925
4.53 | 150 x 50 mm as Rafters | LM | 935.97 | 2.5 | 2339.925
4.54 | 100 x 50 mm as trussed joists and struts | LM | 1864 | 1.5 | 2796
4.55 | 75x50mm purlins | LM | 1580 | 1.5 | 2370
4.56 | 150 x 50 mm as King post | LM | 216 | 1.5 | 324
4.57 | Ditto, wall plate | LM | 202 | 1.5 | 303
4.58 | 25 x 150mm splice plates | LM | 202 | 1.2 | 242.4
4.59 | 25 x 200mm Ridge board | LM | 134 | 1.5 | 201
4.6 | Mild steel |  |  | -
4.61 | 100 × 100 × 100 × 3mm thick angle cleat nailed to timber | NO | 200 | 15 | 3000
4.62 | Boarding |  |  | -
4.63 | WROT CYPRESS, Prime Grade |  |  | -
4.64 | 25x50mm tongued and grooved boarding to eaves | SM | 112 | 6 | 672
4.65 | 32 x 250 mm Fascia board fixed to rafters | LM | 195 | 5 | 975
4.66 | Painting and decorating |  |  | -
4.67 | Knot, prime, stop and apply 3 coats polyurethane varnish to eaves boarding | SM | 112 | 5 | 560
4.68 | Ditto but 3 coats gloss oil paint to fascia board 100-200mm girth | LM | 112 | 5 | 560
4.69 | Rainwater disposal |  |  | -
4.7 | 150x150mm 24gauge galvanized mild steel box gutter with galvanized steel brackets at 600mm centers | LM | 195 | 6 | 1170
4.71 | fixed to fascia board (ms) |  |  | -
4.72 | Ditto, 100mm diameter down pipe fixed with brackets to wall at 1000mm maximum centers | LM | 68 | 2.5 | 170
4.73 | Extra over ditto for 600mm swanneck projection | NO | 30 | 5 | 150
4.74 | Ditto shoe | NO | 30 | 5 | 150
4.75 | Knot, prime, stop and apply 3 coats oil paint externally to: |  |  | -
4.76 | Timber fascia 200-300mm girth | SM | 195 | 5 | 975
4.77 | Metal gutter | SM | 195 | 20 | 3900
| Ceiling Finish |  |  |  | 0
0
| 50 x 50 blandering on timber joists | m2 | 2780 | 1.5 | 4170
0
| 75 x 50 timber joists | m2 | 500 | 1.5 | 750
0
| Supply and fix ceiling board as approved by engineer | m2 | 1100 | 6.5 | 7150
0
0
| Total carried to summary | $ |  |  | 38170.25
0

## 4 SECURITY OFFICE
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL
PROPOSED ……………………………………....
4 | SECTION 4: SECURITY OFFICE
4.1 | ELEMENT NO. 1 : SUB-STRUCTURES (all provisional)
4.11 | Clear site of all bushes and debris. Grab up roots and | sm | 30 |  | 0
| burn the arisings |  |  |  | 0
0
4.1.2 | Excavate over site 200 mm deep to remove vegetable soil and cart away to spoil heap where directed on site | sm | 25 |  | 0
0
4.1.3 | 50mm thick Quarry dust blinding to surfaces of hardcore :rolled smooth to receive polytheen sheeting (m.s) | sm | 32 |  | 0
0
4.1.4 | Spread surplus excavated material on site as directed | cm | 25 |  | 0
0
| Insitu concrete class 25/20 , vibrated and reinforced as described, in:- |  |  |  | 0
4.1.5 | Foundation Strip | cm | 3.6 |  | 0
0
4.1.6 | 100 mm Ground floor slab | sm | 25 |  | 0
0
| Page Total Carried Forward to Next Page |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL
| Total Brought Forward from Previous Page |  |  |  | 0
| Formwork |  |  |  | 0
0
4.1.7 | To the edges of ground slabs 100 - 200mm wide | lm | 20 |  | 0
0
| Reinforcement |  |  |  | 0
0
4.1.8 | Mesh reinforcement reference A142 weighing 2.22kg/m2 in ground slabs | m2 | 25 |  | 0
0
| Anti-termite treatment |  |  |  | 0
0
| Gladiator or equal and approved chemical anti-termite |  |  |  | 0
4.1.9 | treatment, executed complete by an approved specialist |  |  |  | 0
| under a ten-year guarantee, to surfaces of blinding | m2 | 25 |  | 0
0
| Damp-proof membrane |  |  |  | 0
0
4.1.10 | 1000 gauge polythene or other equal and approved | m2 | 25 |  | 0
| damp-proof membrane, laid over blinded hardcore |  |  |  | 0
| (m.s) with 300mm side and end laps (measured |  |  |  | 0
| nett-allow for laps) |  |  |  | 0
0
0
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL
| PAGE TOTAL BROUGHT FORWARD |  |  |  | 0
| SUPER STRUCTURE |  |  |  | 0
0
4.2 | ELEMENT NO. 2: REINFORCED CONCRETE |  |  |  | 0
0
4.2.1 | Reinforced concrete class 25 in |  |  |  | 0
0
4.2.2 | Beams | m3 | 10 |  | 0
0
| Formwork |  |  |  | 0
0
4.2.3 | To sides and soffits of beams | m2 | 50 |  | 0
0
| Reinforcement |  |  |  | 0
0
| High Tensile mild steel reinforcement bars to BS 8666 in Foundations |  |  |  | 0
0
4.2.4 | 12 mm diameter | Kg | 60 |  | 0
0
| ELEMENT NO. 3: WALLING |  |  |  | 0
4.2.5 | 200mm precast concrete concrete block walls bedded and jointed in cement and sand (1:4) mortar | sm | 18 |  | 0
0
| Horizontal Damp Proof Course:one layer of 3-ply bituminous feltor other equal approved (measured nett-allow for laps) ; B.S. 743 Type A bitumen hessian base 150 mm laps (no allowance made for laps); horizontal, 1 no. layer, bedded in cement sand (1:3) mortar |  |  |  | 0
0
4.2.6 | 200mm wide | LM | 52 |  | 0
0
4.3 | ELEMENT NO. 4 : ROOFING |  |  |  | 0
| ROOF COVERING AND RAINWATER DISPOSAL |  |  |  | -
| Roof covering |  |  |  | -
4.3.1 | 28 gauge pre painted IT4 box profile iron sheets on timber structure (ms) | SM | 66 |  | 0
4.3.2 | Ridge or hip cap, 28 gauge prepainted | LM | 6 |  | 0
Structural Timbers
SAWN TREATED CYPRESS, Grade S50, pressure
impregnated
4.3.3 | 100 x 50 mm as trusses and rafters | LM | 50 |  | 0
4.3.4 | 50 x 50 mm as trusses, trussed joists and struts | LM | 92 |  | 0
4.3.5 | 75x50mm purlins and joists and struts | LM | 60 |  | 0
4.3.6 | 100 x 50 mm as King post | LM | 6 |  | 0
4.3.7 | Ditto, wall plate | LM | 42 |  | 0
| PAGE TOTAL CARRIED FORWARD |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL
| PAGE TOTAL BROUGHT FORWARD |  |  |  | 0
4.3.8 | 25 x 200mm Ridge board | LM | 6 |  | 0
4.3.9 | Dittob but for Fascia Board | LM | 12 |  | 0
Rainwater disposal
4.3.10 | 150x150mm 24gauge galvanized mild steel box gutter with galvanized steel brackets at 600mm centers fixed to fascia board (ms) | LM | 12 |  | 0
4.3.11 | Ditto, 100mm diameter down pipe fixed with brackets to wall at 1000mm maximum centers | LM | 4 |  | 0
4.3.12 | Extra over ditto for 600mm swanneck projection | NO | 4 |  | 0
4.3.13 | Ditto shoe | NO | 4 |  | 0
4.3.14 | Knot, prime, stop and apply 3 coats oil paint externally to:
4.3.15 | Timber fascia 200-300mm girth | LM | 12 |  | 0
4.3.16 | Metal gutter | LM | 12 |  | 0
0
4.4 | ELEMENT NO. 5 : WINDOWS
Extruded anodised aluminium sliding frame 80x50mm mosquito netting and fabricated aluminium burglar proof grill with 6mm thick glass with blue anti-glare film.
4.4.1 | Overall size 1500 x1500mm high | No. | 7 |  | 0
0
4.4.2 | Overall size 2000 x1500mm high | No. | 2 |  | 0
0
4.4.3 | Precast concrete window cill size 260 x 50mm Thick sunk - weathered and throated and bedded and jointed in cement sand mortar | lm | 15 |  | 0
4.5 | ELEMENT NO. 6: DOORS
Internal Doors
4.5.1 | 45 mm thick solid steel panelled double door overall size 1200mm * 2400mm high with and including 150*50 mm steel frame, 3 pairs heavy duty brass butt hinges and 5 lever UNION ribitted door lock | No. | 1 |  | 0
0
| External Doors |  |  |  | 0
4.5.2 | 45 mm thick solid steel panelled double door overall size 1200mm * 2400mm high with and including 150*50 mm steel frame, 3 pairs heavy duty brass butt hinges and 5 lever UNION ribitted door lock | No. | 2 |  | 0
0
| PAGE TOTAL CARRIED FORWARD | $ |  |  | 0
ITEM | DESCRIPTION | UNIT | QTY |  | TOTAL
| PAGE TOTAL BROUGHT FORWARD |  |  |  | 0
4.6 | ELEMENT NO. 7 : FINISHES |  |  |  | 0
| Floor Finishes |  |  |  | 0
| Cement and sand (1:3) screeds, backings, beds etc |  |  |  | 0
4.6.1 | 25mm Thick cement/sand (1:4) screed to receive Ceramic |  |  |  | 0
| floor tiles (measured separately) | SM | 25 |  | 0
| Lightweight water proofed screeds and plaster |  |  |  | 0
| Non-slip 300x300mm ceramic Tiles from approved supplier fixed |  |  |  | 0
| with approved tile adhesive: |  |  |  | 0
| jointed and pointed in approved grout. |  |  |  | 0
4.6.2 | Floor tiles | m2 | 25 |  | 0
0
| Skirtings; |  |  |  | 0
4.6.3 | 100mm wide with rounded junction with wall finish and coved junction with floor finish | lm | 42 |  | 0
0
| Wall Finish |  |  |  | 0
| Plastered surfaces |  |  |  | 0
4.6.4 | Internal Lime Plaster | sm | 160 |  | 0
0
4.6.5 | 15 mm cement and sand (1:3) External cement sand rendering | sm | 160 |  | 0
0
| Glazed tiles |  |  |  | 0
4.6.6 | 6 mm glazed wall tiles fixed to plastered surfaces with approved adhesive to a height of 1200 mm in kitchen areas above counter top | sm | 84 |  | 0
0
| Painting |  |  |  | 0
| Fill uneven surfaces with stucco filler to approval and apply two coats soft white external textured paint to: |  |  |  | 0
0
4.6.7 | Plastered and rendered surfaces | sm | 236 |  | 0
| Prepare and apply two undercoats of brilliant white emulsion paint |  |  |  | 0
| (RAL Code 9001) and two finishing coats of first quality brilliant white |  |  |  | 0
| Silk Vinyl emulsion paint (RAL Code 9001) to;- |  |  |  | 0
0
4.6.8 | Plastered surfaces internally and externally | sm | 236 |  | 0
| PAGE TOTAL CARRIED TO MAIN SUMMARY | $ |  |  | 0
ITEM | DESCRIPTION | UNIT | QTY |  | TOTAL
0
4.7 | ELEMENT NO. 7 : ELECTRICAL INSTALLATIONS |  |  |  | 0
0
| Lighting Fittings |  |  |  | 0
0
| Supply and install following lighting fixtures with all accessories |  |  |  | 0
| as per the specifications and drawings and complete with lamp |  |  |  | 0
| fitting and accessories of Engineer or approved make. |  |  |  | 0
0
4.7.1 | Type 4S - 4x18w surface mount flourescent light fitting as |  |  |  | 0
| Phillips or equivalent | No. | 42 |  | 0
4.7.2 | Type 4S - 2x18w surface mount flourescent light fitting
| Phillips or equivalent | No. | 14 |  | 0
4.7.3 | Type W1 - 1x36w Surface mounted waterproof polycarbonate flourescent light fitting | No. | 8 |  | 0
4.7.4 | 150W LED floodlight | No. | 4 |  | 0
Switches
4.7.5 | 5 Amps one gang one way switch | No | 24 |  | 0
4.7.6 | 5 Amps two gang one way switch | No | 8 |  | 0
0
| Socket outlets |  |  |  | 0
0
| Supply and installation of fused shuttered switched socket outlet to comply with relevant BS standard (Clipsal, Orange, Crabtree/ Tenby/ABB or equivalent). Wiring (including supply of earth wire and all other material required) of above socket outlet using approved type 2.5mm² PVC/PVC copper cable and 2.5mm² earth wire drawn through securely fixed concealed PVC conduit in a ring circuit.Socket outlet points |  |  |  | 0
4.7.8 | 13 A twin sockets outlet | No | 72 |  | 0
| Page Total Carried to Forward |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QTY |  | TOTAL
| Page Total Brought Forward |  |  |  | 0
Cables, Cable pathways and Conduits
Supply, install, test and commission 450/750 volts 6491X cables with all required accessories for proper installation and operation including conduits, pipes( each cable in separate conduit or pipe), cable lugs, ties... etc. as shown on drawing, as per the preamble, the specifications and supervision engineer's requirements.
4.7.9 | Supply, install and connect complete 1.5 sq. mm colour-coded SC cables to lighting points drawn in Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | M | 400 |  | 0
4.7.10 | Supply and install two compartment floor recessed metallic electrical floor box with flap cover complete with lifting handle, cable cable flaps, as Crabtree Britmac or equal and approved | No. | 1 |  | 0
Allow for structured cabling with network points as described neatly
4.7.11 | concealed in 4x2" metal trunking | LS | 1 |  | 0
4.7.12 | Supply, Deliver, Install, Test and Commission the following AC indoor units including with all accessories including all connections as described. Wall mounted unit of cooling capacity: 12.3kW with inbuilt drain pump, power input: 0.15kW, single phase, Refrigerant R-410A complete with all hanging accessories, remote control, filter chamber, drain pump kit, suction canvas, ceiling panel, wiring from DP switch to fan coil unit, fabricated steel mounting brackets, steel frames and raw bolts, anti-vibration mountings. DP switch to be positioned next to the in door unit. The indoor unit shall be to Daikin/Toshiba/LG make or approved equivalent. | No. | 1 |  | 0
| TOTAL FOR SECTION 5: CARRIED TO GRAND SUMMARY |  |  |  | 0

## 5 MAIN TOILET
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
GRANT No. ……………………………………….
PROPOSED ……………………………………....
…….………………………………….. DISTRICT
5 | SECTION 5: MAIN TOILET
5.1 | ELEMENT NO. 1 : SITE PREPARATION
5.1.1 | Clear site of all bushes and debris. Grab up roots and | m2 | 44 |  | 0
| burn the arisings |  |  |  | 0
0
5.1.2 | Load, wheel and cart deposit and spread surplus excavated |  |  |  | 0
| material where directed on site at a distance not exceeding |  |  |  | 0
| 100 meters | Item | 1 |  | 0
0
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PAGE TOTAL BROUGHT FORWARD
5.2 | ELEMENT NO. 2 : SUBSTRUCTURES (PROVISIONAL)
Excavations including maintaining and supporting sides
and keeping free from water, mud and fallen material
5.2.1 | Top soil excavation average 200mm deep | m2 | 44 |  | 0
5.2.2 | Excavate trench for foundation not exceeding 1.50 |  |  |  | 0
| meters deep, starting from stripped levels | m3 | 40.8 |  | 0
0
| Planking and strutting |  |  |  | 0
5.2.3 | Allow for keeping foundations free from water, mud, fallen |  |  |  | 0
| materials, etc. | LS | 1 |  | 0
0
| Disposal |  |  |  | 0
5.2.4 | Return, fill and ram selected excavated material around |  |  |  | 0
| foundations | m3 | 16.32
5.2.5 | Load, wheel and cart deposit and spread surplus |  |  |  | 0
| excavated material where directed on site at a |  |  |  | 0
| distance not exceeding 100 meters | m3 | 24.48 |  | 0
0
| Hardcore or other approved filling, as described |  |  |  | 0
5.2.6 | 300mm thick well compacted hardcore filling blinded with |  |  |  | 0
| 25mm thick quarry dust layer to receive surface bed | m2 | 44 |  | 0
5.2.7 | 50mm thick Quarry dust blinding to surfaces of hardcore :rolled | m2 | 44 |  | 0
| smooth to receive polytheen sheeting (m.s) |  |  |  | 0
0
| Anti-termite treatment |  |  |  | 0
0
5.2.8 | Gladiator or equal and approved chemical anti-termite |  |  |  | 0
| treatment, executed complete by an approved specialist |  |  |  | 0
| under a ten-year guarantee, to surfaces of blinding | m2 | 44 |  | 0
| Damp-proof membrane |  |  |  | 0
5.2.9 | 1000 gauge polythene or other equal and approved |  |  |  | 0
| damp-proof membrane, laid over blinded hardcore |  |  |  | 0
| (m.s) with 300mm side and end laps (measured |  |  |  | 0
| nett-allow for laps) | m2 | 44 |  | 0
0
| Reference A142 mesh 200 x 200 mm , weight 2.22 kgs per |  |  |  | 0
| square meter ( measured net - no allowance made for laps |  |  |  | 0
| (inclunding bends, tying wire and distance blocks) |  |  |  | 0
5.2.10 | Fabric ref. A142 weighing 2.22kg/ sq.metre, in surface bed | m2 | 44 |  | 0
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PAGE TOTAL BROUGHT FORWARD
5.3 | ELEMENT NO. 3 : CONCRETE WORKS
Plain concrete class 15 in:
5.3.1 | 50mm blinding | m2 | 27.2 |  | 0
0
| Insitu concrete class 25/20 , vibrated and reinforced as described, in:- |  |  |  | 0
0
| BEAMS |  |  |  | 0
0
5.3.2 | Ground beam | m3 | 8.16 |  | 0
0
5.3.3 | Ring beam 1 | m3 | 3.06 |  | 0
0
| SLABS |  |  |  | 0
0
5.3.4 | 200mm thick surface bed laid in bays including all |  |  |  | 0
| necessary formwork | m3 | 6.84 |  | 0
0
| Reinforcement, as described:-[PROVISIONAL] |  |  |  | 0
0
| High yield square twisted reinforcement bars to B.S 4461 |  |  |  | 0
0
| BEAMS |  |  |  | 0
0
5.3.5 | Ditto for Y12 as main bars | Kg | 120.768 |  | 0
0
5.3.6 | Ditto for R8 as rings | Kg | 126.6084 |  | 0
0
| Sawn formwork as described to:- |  |  |  | 0
0
5.3.7 | To edge of floor slab | m2 | 5.1 |  | 0
0
5.3.8 | Ditto to sides and soffits of roof slab | m2 | 50 |  | 0
0
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PAGE TOTAL BROUGHT FORWARD
5.4 | ELEMENT NO. 4 : WALLING
SUB-STRUCTURE WALLING
Approved compacted hardcore fill bedded and jointed in
cement sand mortar (1:4)
5.4.1 | 400mm thick rubble stone foundation walling | m3 | 16.32 |  | 0
0
| SUPER-STRUCTURE WALLING |  |  |  | 0
0
| 200x400mm hollow block walling bedded and jointed in |  |  |  | 0
| cement and sand (1:4) mortar, reinforcement with and |  |  |  | 0
| including 25mm wide x 20 gauge hoop iron at every |  |  |  | 0
| alternate course as described in: |  |  |  | 0
0
5.4.2 | 200 mm thick reinforced in every second course | m2 | 138 |  | 0
0
| Horizontal Damp Proof Course:one layer of 3-ply bituminous felt |  |  |  | 0
| or other equal approved (measured nett-allow for laps) |  |  |  | 0
0
5.4.3 | 200mm wide; B.S. 743 Type A bitumen hessian base 150 mm laps (no allowance made for laps); horizontal, 1 no. layer, bedded in cement sand (1:3) mortar | LM | 34 |  | 0
0
5.4.4 | PCC coping above parapet wall | LM | 12 |  | 0
0
0
0
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PAGE TOTAL BROUGHT FORWARD
5.5 | ROOF COVERING AND RAINWATER DISPOSAL |  |  |  | -
| (PROVISIONAL) |  |  |  | -
| Roof covering |  |  |  | -
5.5.1 | 28 gauge pre painted galvanized corrugated iron sheets on timber structure (ms) | SM | 7 |  | 0
5.5.2 | Ridge or hip cap, 28 gauge prepainted | LM | 11 |  | 0
Structural Timbers
SAWN TREATED CYPRESS, Grade S50, pressure
impregnated (Provisional)
5.5.3 | 100 x 50 mm as trussed rafters, joists and struts | LM | 41.6 |  | 0
5.5.4 | 75x50mm purlins | LM | 62 |  | 0
5.5.5 | 100x50mm Hip rafters | LM | 22 |  | 0
5.5.6 | Ditto, wall plate | LM | 22 |  | 0
5.5.7 | 25 x 150mm splice plates | LM | 22 |  | 0
5.5.8 | 25 x 200mm Ridge board | LM | 12 |  | 0
Mild steel
5.5.9 | 100 × 100 × 100 × 3mm thick angle cleat nailed to timber | NO | 25 |  | 0
Boarding
WROT CYPRESS, Prime Grade
5.5.11 | 32 x 250 mm Fascia board fixed to rafters | LM | 22 |  | 0
Painting and decorating
5.5.13 | Ditto but 3 coats gloss oil paint to fascia board 100-200mm girth | LM | 22 |  | 0
Rainwater disposal
5.5.14 | 150x150mm 24gauge galvanized mild steel box gutter with galvanized steel brackets at 600mm centers | LM | 22 |  | 0
fixed to fascia board (ms)
5.5.15 | Ditto, 100mm diameter down pipe fixed with brackets to wall at 1000mm maximum centers | LM | 18 |  | 0
5.5.16 | Extra over ditto for 600mm swanneck projection | NO | 6 |  | 0
5.5.17 | Ditto shoe | NO | 6 |  | 0
5.5.18 | Knot, prime, stop and apply 3 coats oil paint externally to:
5.5.19 | Timber fascia 200-300mm girth | LM | 22 |  | 0
5.5.20 | Metal gutter | SM | 22 |  | 0
5.5.21 | Prepare and apply bituminous paint to inside of gutter | SM | 22 |  | 0
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PAGE TOTAL BROUGHT FORWARD
5.6 | ELEMENT NO. 6 : FINISHES
Floor Finishes
Cement and sand (1:3) screeds, backings, beds etc
5.6.1 | 25mm Thick cement/sand (1:4) screed steel trowelled finish | m2 | 44 |  | 0
0
| Skirtings; |  |  |  | 0
5.6.3 | Junction with floor finish | m2 | 6.2 |  | 0
0
5.6.4 | Ditto for edge of steps and slab | m2 | 4.35 |  | 0
0
| Wall Finish |  |  |  | 0
0
| 15 mm cement and sand (1:3) render, finished with |  |  |  | 0
| woodfloat to:- |  |  |  | 0
0
5.6.5 | Concrete or masonry surfaces internally and externally |  |  |  | 0
| Painting | m2 | 273 |  | 0
0
| Fill uneven surfaces with stucco filler to approval and apply |  |  |  | 0
| two coats soft white external textured paint to: |  |  |  | 0
0
5.6.6 | Plastered and rendered surfaces | m2 | 273 |  | 0
0
| Prepare and apply two undercoats of brilliant white emulsion paint (RAL Code 9001) and two finishing coats of first quality brilliant white Silk Vinyl emulsion paint (RAL Code 9001) to;- |  |  |  | 0
0
5.6.7 | Plastered surfaces internally and externally | m2 | 273 |  | 0
0
5.6.8 | Vent grills | LS | 1 |  | 0
0
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PAGE TOTAL BROUGHT FORWARD
5.7 | ELEMENT NO. 7 : ELECTRICAL INSTALLATIONS
Lighting Fittings
Supply and install following lighting fixtures with all accessories
as per the specifications and drawings and complete with lamp
fitting and accessories of Engineer or approved make.
5.7.1 | Type 4S - 4x18w surface mount flourescent light fitting | No. | 6 |  | 0
5.7.2 | Type W1 - 1x36w Surface mounted waterproof polycarbonate
| flourescent light fitting | No. | 1 |  | 0
Switches
5.7.3 | 5 Amps two gang one way switch | No | 2 |  | 0
Socket outlets
Supply and installation of fused shuttered switched socket outlet
to comply with relevant BS standard (Clipsal, Orange, Crabtree/
Tenby/ABB or equivalent). Wiring (including supply of earth wire
and all other material required) of above socket outlet using approved type 2.5mm² PVC/PVC copper cable and 2.5mm² earth wire drawn through securely fixed concealed PVC conduit in a ring circuit.
Socket outlet points
5.7.4 | 13 A twin sockets outlet | No | 2 |  | 0
Cables, Cable pathways and Conduits
Supply, install, test and commission 450/750 volts 6491X cables with all required accessories for proper installation and operation including
conduits, pipes( each cable in separate conduit or pipe), cable lugs, ties... etc. as shown on drawing, as per the preamble, the specifications and supervision engineer's requirements.
5.7.5 | Supply, install and connect complete 1.5 sq. mm colour-coded SC cables to lighting points drawn in Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories | M | 20 |  | 0
5.7.6 | Supply and install two compartment floor recessed metallic electrical floor box with flap cover complete with lifting handle, cable cable flaps, as Crabtree Britmac or equal and approved | No. | 1 |  | 0
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PAGE TOTAL BROUGHT FORWARD
5.8 | TOILET PIT
Excavations including maintaining and supporting sides
and keeping free from water, mud and fallen material
5.8.1 | Stripping of surface and excavation for latrine pit in soft soil up to depth of approximately 1.8m; pit dimensions: 3m width x 11m length | C.M | 59.4 |  | 0
5.8.2 | Excavation for latrine pit in hard rock at a depth approximately starting is not encountered, the excavation rates in soft soil will apply at these depths) | C.M | 15 |  | 0
Reinforced concrete class 25,
5.8.3 | 150mm thick vibrated reinforced concrete for bottom | C.M | 1.88 |  | 0
slab (concrete class 20)
Reinforcement, as described (PROVISIONAL)
High yield square twisted reinforcement to BS 4461
5.8.4 | 10mm high tensile square twisted bars; cold worked; BS4461 | KG | 130 |  | 0
including bends, hooks, tying wire, distance blocks and spacers
for bottom slab; Y10@ 200mm c/c .
5.8.5 | Supply and fix sawn formwork to sides of bottom slab | L.M | 12.5 |  | 0
200x400mm block walling bedded and jointed in
cement and sand (1:4) mortar, reinforcement with and
including 25mm wide x 20 gauge hoop iron at every
alternate course as described in:
5.8.6 | Sub-Structure walling | S.M | 32 |  | 0
Cement and sand (1:3) screeds, backings, beds etc
5.8.7 | 15mm thick two coat cement sand (1:3) plaster trowelled smooth and | S.M | 62.5 |  | 0
comprising 12mm backing and 3mm finishing coat for internal walls.
| Page Total Carried to Summary |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
| Total Carried from previous Page |  |  |  | 0
Reinforced concrete class 25,
5.8.8 | Supply all materials and cast a 125mm thick vibrated reinforced | C.M | 1.6 |  | 0
concrete slab, mix1:2:4 or class 20/20. Top slab dimensions 2.5m x 5.0m
Reinforcement, as described (PROVISIONAL)
High yield square twisted reinforcement to BS 4461
5.8.9 | 10mm high tensile square twisted bars; cold worked; BS4461 | KG | 130 |  | 0
including bends, hooks, tying wire, distance blocks and spacers for top slab; Y10@ 200mm c/c .
5.8.10 | Supply and fix sawn formwork to sides of bottom slab | L.M | 12.5 |  | 0
5.8.11 | Supply and fix sawn formwork beneath the slab | S.M | 12.5 |  | 0
5.8.12 | Manhole frame and covers | Pcs. | 4 |  | 0
5.8.13 | Tank piping, fittings and accessories which includes among others ring bearers anchored in the wall and a 2.5 m heigh 4'' vent pipe with rain cower and fly net | Item | 1 |  | 0
5.8.14 | 4" brown sewer pipes with accessories laid with 1% slope in trench | L.M | 12 |  | 0
of 0.5 to 0.8 m depth
Reinforced concrete class 25,
5.8.15 | Supply all materials and cast R.C. buffer beam, 100mm wide x 450mm deep, | C.M | 0.3 |  | 0
concrete class 20
5.8.16 | 12mm high tensile square twisted bars; cold worked; BS4461 including | KG | 22 |  | 0
bends, hooks, tying wire, distance blocks and spacers for ring beam
reinforcement, 4Y12
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PAGE TOTAL BROUGHT FORWARD
5.9 | ELEMENT NO. 9 : OPENINGS
WINDOWS
Extruded anodised aluminium sliding frame 80x50mm mosquito
netting and fabricated aluminium burglar proof grill with 6mm thick
glass with blue anti-glare film.
5.9.1 | Overall size 600 x 800mm high | No. | 8 |  | 0
0
5.9.2 | Overall size 1000 x 1200mm high | No. | 2 |  | 0
0
5.9.3 | Precast concrete window cill size 260 x 50mm Thick sunk - weathered |  |  |  | 0
| and throated and bedded and jointed in cement sand mortar | No. | 10 |  | 0
0
| VENT BLOCKS |  |  |  | 0
0
5.9.4 | 2000mm x 800mm | No. | 50 |  | 0
0
0
| DOORS |  |  |  | 0
| 45mm thick solid core flush door to B.S 459: parts faced both |  |  |  | 0
| sides with 6mm mahogany veneered plywood and lipped on |  |  |  | 0
| all edges in hardwood, including all planted moulding. |  |  |  | 0
| Complete with hinges and locks |  |  |  | 0
0
5.9.5 | 50mm thick door overall size 900x2150mm high | No. | 8 |  | 0
0
5.9.6 | 50mm thick door overall size 900x2150mm high | No. | 2 |  | 0
0
| Supply delivery and fix the following ironmongery |  |  |  | 0
| with matching screws |  |  |  | 0
0
5.9.7 | 100mm heavy duty butt hinges | No. | 30 |  | 0
0
5.9.8 | 3 lever mortice lock as Union 2277complete with |  |  |  | 0
| Union 2277 683 -06 -2 brass lever furniture | No. | 2 |  | 0
0
5.9.10 | 100mm thick permanet ventilation blocks over openings | LS | 1 |  | 0
0
| TOTAL CARRIED TO GRAND SUMMARY |  |  |  | 0

## 6 SECURITY TOILET
ITEM | DESCRIPTION | UNIT | QNTY | RATE | AMT US$
GRANT No. ……………………………………….
PROPOSED ……………………………………....
…….………………………………….. DISTRICT
6 | SECTION 6: SECURITY TOILET
ELEMENT NO. 1 : SITE PREPARATION
6.1.1 | Clear site of all bushes and debris. Grab up roots and | m2 | 11.89 |  | 0
burn the arisings
6.1.2 | Load, wheel and cart deposit and spread surplus excavated material where directed on site at a distance not exceeding 100 meters | Item | 1 |  | 0
6.2 | ELEMENT NO. 2 : SUBSTRUCTURES (PROVISIONAL)
Excavations including maintaining and supporting sides
and keeping free from water, mud and fallen material
6.2.1 | Top soil excavation average 200mm deep | m2 | 11.89 |  | 0
6.2.2 | Excavate trench for foundation not exceeding 1.50
| meters deep, starting from stripped levels | m3 | 16 |  | 0
Planking and strutting
6.2.3 | Allow for keeping foundations free from water, mud, fallen
| materials, etc. | LS | 1 |  | 0
Disposal
6.2.4 | Return, fill and ram selected excavated material around
| foundations | m3 | 16 |  | 0
6.2.5 | Load, wheel and cart deposit and spread surplus
excavated material where directed on site at a
| distance not exceeding 100 meters | m3 | 16 |  | 0
Hardcore or other approved filling, as described
6.2.6 | 300mm thick well compacted hardcore filling blinded with 25mm thick quarry dust layer to receive surface bed | m2 | 4.756 |  | 0
6.2.7 | 50mm thick Quarry dust blinding to surfaces of hardcore :rolled smooth to receive polytheen sheeting (m.s) | m2 | 0.5945 |  | 0
Anti-termite treatment
6.2.8 | Gladiator or equal and approved chemical anti-termite
treatment, executed complete by an approved specialist
| under a ten-year guarantee, to surfaces of blinding | m2 | 4.756 |  | 0
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QNTY | RATE | AMT US$
PAGE TOTAL BROUGHT FORWARD
Damp-proof membrane
6.2.9 | 1000 gauge polythene or other equal and approved
damp-proof membrane, laid over blinded hardcore
(m.s) with 300mm side and end laps (measured
| nett-allow for laps) | m2 | 4.756 |  | 0
Reference A142 mesh 200 x 200 mm , weight 2.22 kgs per square meter ( measured net - no allowance made for laps (inclunding bends, tying wire and distance blocks)
6.2.10 | Fabric ref. A142 weighing 2.22kg/ sq.metre, in surface
| bed | m2 | 4.756 |  | 0
6.3 | ELEMENT NO. 3 : CONCRETE WORKS
Plain concrete class 15 in:
6.3.1 | 50mm blinding | m2 | 9.6 |  | 0
Insitu concrete class 25/20 , vibrated and reinforced as described, in:-
6.3.2 | Beams | m3 | 1.5 |  | 0
6.3.3 | 200mm thick surface bed laid in bays including all
| necessary formwork | m3 | 1.7 |  | 0
Reinforcement, as described:-[PROVISIONAL]
High yield square twisted reinforcement bars to B.S 4461
BEAMS
6.3.4 | Ditto for Y12 as main bars | Kg | 85.248 |  | 0
6.3.5 | Ditto for R8 as rings | Kg | 67.1296 |  | 0
Sawn formwork as described to:-
6.3.6 | To edge of floor slab | m2 | 3.2 |  | 0
6.3.7 | Ditto to sides and soffits of roof slab | m2 | 23.66 |  | 0
6.3.8 | Ditto to sides of steps | m2 | 19.2 |  | 0
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QNTY | RATE | AMT US$
PAGE TOTAL BROUGHT FORWARD
6.4 | ELEMENT NO. 4 : WALLING
SUB-STRUCTURE WALLING
Approved compacted hardcore fill bedded and jointed in
cement sand mortar (1:4)
6.4.1 | 400mm thick rubble stone foundation walling | m3 | 9.6 |  | 0
SUPER-STRUCTURE WALLING
200x400mm hollow block walling bedded and jointed in
cement and sand (1:4) mortar, reinforcement with and
including 25mm wide x 20 gauge hoop iron at every
alternate course as described in:
6.4.2 | 200 mm thick reinforced in every third course | m2 | 48 |  | 0
Horizontal Damp Proof Course:one layer of 3-ply bituminous felt
or other equal approved (measured nett-allow for laps)
6.4.3 | 200mm wide; B.S. 743 Type A bitumen hessian base 150 mm laps
(no allowance made for laps); horizontal, 1 no. layer, bedded in
| cement sand (1:3) mortar | LM | 16 |  | 0
6.4.4 | PCC coping above parapet wall | LM | 16 |  | 0
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QNTY | RATE | AMT US$
PAGE TOTAL BROUGHT FORWARD
ELEMENT NO. 5 : ROOF FINISHES
6.5 | ROOF COVERING AND RAINWATER DISPOSAL
(PROVISIONAL)
Roof covering
6.5.1 | 28 gauge pre painted galvanized corrugated iron sheets on timber structure (ms) | SM | 12
6.5.2 | Ridge or hip cap, 28 gauge prepainted | LM | 4.1
Structural Timbers
SAWN TREATED CYPRESS, Grade S50, pressure
impregnated (Provisional)
6.5.3 | 100 x 50 mm as trussed rafters, joists and struts | LM | 16
6.5.4 | 75x50mm purlins | LM | 31
6.5.5 | 100x50 mm Hip rafters | LM | 8.2
6.5.6 | Ditto, wall plate | LM | 8.2
6.5.7 | 25 x 150mm splice plates | LM | 8.2
6.5.8 | 25 x 200mm Ridge board | LM | 8.2
6.5.9 | Mild steel
6.5.10 | 100 × 100 × 100 × 3mm thick angle cleat nailed to timber | NO | 6
Boarding
6.5.11 | WROT CYPRESS, Prime Grade
6.5.13 | 32 x 250 mm Fascia board fixed to rafters | LM | 9
Painting and decorating
6.5.15 | Ditto but 3 coats gloss oil paint to fascia board 100-200mm girth | LM | 9
4.69 | Timber fascia 200-300mm girth | LM | 9
| Total carried to summary | $
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QNTY | RATE | AMT US$
PAGE TOTAL BROUGHT FORWARD
6.6 | ELEMENT NO. 6 : FINISHES
Floor Finishes
Cement and sand (1:3) screeds, backings, beds etc
6.6.1 | 25mm Thick cement/sand (1:4) screed to steel trowelled finish | m2 | 11.89 |  | 0
6.6.3 | Skirtings;
100mm wide with rounded junction with wall finish and coved junction
| with floor finish | m2 | 1.2 |  | 0
6.6.4 | Ditto for edge of steps and slab | m2 | 19.2 |  | 0
Wall Finish
15 mm cement and sand (1:3) render, finished with
woodfloat to:-
6.6.5 | Concrete or masonry surfaces internally and externally
| Painting | m2 | 48 |  | 0
Fill uneven surfaces with stucco filler to approval and apply two coats soft white external textured paint to:
6.6.6 | Plastered and rendered surfaces | m2 | 48 |  | 0
Prepare and apply two undercoats of brilliant white emulsion paint
(RAL Code 9001) and two finishing coats of first quality brilliant white
Silk Vinyl emulsion paint (RAL Code 9001) to;-
6.6.7 | Plastered surfaces internally and externally | m2 | 48 |  | 0
6.6.8 | Vent grills | LS | 1 |  | 0
| Total carried to Main summary | $ |  |  | 0
ITEM | DESCRIPTION | UNIT | QNTY |  | AMT US$
ELEMENT NO. 7 : ELECTRICAL INSTALLATIONS
Lighting Fittings
6.7.1 | Supply and install following lighting fixtures with all accessories as per the specifications and drawings and complete with lamp fitting and accessories of Engineer or approved make.
6.7.2 | Type 4S - 4x18w surface mount flourescent light fitting | No. | 2 |  | 0
6.7.3 | Type W1 - 1x36w Surface mounted waterproof polycarbonate flourescent light fitting | No. | 1 |  | 0
Switches
6.7.4 | 5 Amps two gang one way switch | No | 1 |  | 0
Socket outlets
Supply and installation of fused shuttered switched socket outlet to comply with relevant BS standard (Clipsal, Orange, Crabtree/ Tenby/ABB or equivalent). Wiring (including supply of earth wire and all other material required) of above socket outlet using approved type 2.5mm² PVC/PVC copper cable and 2.5mm² earth wire drawn through securely fixed concealed PVC conduit in a ring circuit.
Socket outlet points
6.7.5 | 13 A twin sockets outlet | No | 1 |  | 0
Cables, Cable pathways and Conduits
Supply, install, test and commission 450/750 volts 6491X cables with all required accessories for proper installation and operation including conduits, pipes( each cable in separate conduit or pipe), cable lugs, ties... etc. as shown on drawing, as per the preamble, the specifications and supervision engineer's requirements.
6.7.6 | Supply, install and connect complete 1.5 sq. mm colour-coded SC cables to lighting points drawn in Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | M | 10 |  | 0
6.7.7 | Supply and install two compartment floor recessed metallic electrical
floor box with flap cover complete with lifting handle, cable cable flaps,
| as Crabtree Britmac or equal and approved | No. | 1
| PAGE TOTAL CARRIED TO SUMMARY | $ |  |  | 0
ITEM | DESCRIPTION | UNIT | QNTY |  | AMT US$
6.8 | TOILET PIT
Excavations including maintaining and supporting sides
and keeping free from water, mud and fallen material
6.81 | Stripping of surface and excavation for latrine pit in soft soil up to depth of | C.M | 14.4 |  | 0
approximately 1.8m; pit dimensions: 2m width x 4m length
6.82 | Excavation for latrine pit in hard rock at a depth approximately starting at 1.8 M | C.M | 15 |  | 0
Reinforced concrete class 25,
6.8.3 | 150mm thick vibrated reinforced concrete for bottom | C.M | 1.2 |  | 0
slab (concrete class 20)
Reinforcement, as described (PROVISIONAL)
High yield square twisted reinforcement to BS 4461
6.8.4 | 10mm high tensile square twisted bars; cold worked; BS4461 including bends, hooks, tying wire, distance blocks and spacers for bottom slab; Y10@ 200mm c/c . | KG | 130 |  | 0
6.8.5 | Supply and fix sawn formwork to sides of bottom slab | L.M | 12.5 |  | 0
200x400mm block walling bedded and jointed in
cement and sand (1:4) mortar, reinforcement with and
including 25mm wide x 20 gauge hoop iron at every
alternate course as described in:
6.8.6 | Sub-Structure walling | S.M | 22 |  | 0
Cement and sand (1:3) screeds, backings, beds etc
6.8.7 | 15mm thick two coat cement sand (1:3) plaster trowelled smooth and comprising 12mm backing and 3mm finishing coat for internal walls. | S.M | 22 |  | 0
Reinforced concrete class 25,
6.8.8 | Supply all materials and cast a 125mm thick vibrated reinforced | C.M | 1.2 |  | 0
concrete slab, mix1:2:4 or class 20/20. Top slab dimensions 2.5m x 5.0m
| Page Total Carried to Next Page |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QNTY |  | AMT US$
| Page Total Carried Forward from previous Page |  |  |  | 0
Reinforcement, as described (PROVISIONAL)
High yield square twisted reinforcement to BS 4461
6.8.9 | 10mm high tensile square twisted bars; cold worked; BS4461 | KG | 65 |  | 0
including bends, hooks, tying wire, distance blocks and spacers for
top slab; Y10@ 200mm c/c .
6.8.10 | Supply and fix sawn formwork to sides of bottom slab | L.M | 12.5 |  | 0
6.8.11 | Supply and fix sawn formwork beneath the slab | S.M | 12.5 |  | 0
6.8.12 | Manhole frame and covers | Pcs. | 1 |  | 0
6.8.13 | Tank piping, fittings and accessories which includes among others ring bearers anchored in the wall and a 2.5 m heigh 4'' vent pipe with rain cower and fly net | Item | 1 |  | 0
6.8.14 | 4" brown sewer pipes with accessories laid with 1% slope in trench of 0.5 to 0.8 m depth | L.M | 12 |  | 0
Reinforced concrete class 25,
6.8.15 | Supply all materials and cast R.C. buffer beam, 100mm wide x 450mm deep, concrete class 20 | C.M | 0.3 |  | 0
6.8.16 | 12mm high tensile square twisted bars; cold worked; BS4461 including bends, hooks, tying wire, distance blocks and spacers for ring beam reinforcement, 4Y12 | KG | 22 |  | 0
SECUTRITY TOILET SUMMARY
BUILDERS WORKS TOTAL
ELECTRICAL WORKS TOTAL
PIT LATRINE TOTAL
TOTAL CARRIED TO GRAND SUMMARY

## 7 SECURITY FENCES
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE (US$) | AMOUNT (US$)
GRANT No. ……………………………………….
PROPOSED ……………………………………....
7 | SECTION 7: SECURITY FENCES
7.1 | Clear site of all bushes, grab up roots and burn their arisings | SM | 64 |  | 0
7.2 | ELEMENT NO.2: BARBED WIRE FENCING |  |  |  | 0
| Excavations |  |  |  | 0
7.2.1 | Excavate starting from ground level pits size 600mm deep by 300mm Diameter and load to spread soil on site | No | 162 |  | 0
7.2.3 | Cast Reinforced concrete mix 1:2:4 mixed aggregates to 600mm deep x 300mm diameter pits; including curing as required | CM | 7 |  | 0
| The contractor is reminded to include in his pricing, the cost of supply, cutting, waste and erecting and all other necessary fittings including welding lugs onto the angle bars etc. Steel sections and the necessary fixing and anchorage to be treated as described in the specifications. |  |  |  | 0
| Fencing |  |  |  | 0
7.2.4 | Supply and fix in concrete foundation 3m long 50mm x 50mm x 3mm mild steel angles (2.34kg/m) with welded lugs for anchorage including priming with red oxide primer before delivery to site. This should include 2 nos. steel 50mm x 50mm x 3mm angle sections (both sides of the angle bar at a height of 1m) for corner props and in every 25m. | No | 162 |  | 0
7.2.4 | Supply and fix 12.5 Gauge barbed wire (7 strands) fixed to the 50mm x 50mm x 3mm steel angles by binding wire. Cost should include the cost of binding wire, cutting, tying and fixing. One strand to anchor the chain link under the ground and to be backfilled | LM | 2240 |  | 0
| Total Carried to Summary |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE (US$) | AMOUNT (US$)
7.3 | Hesco Fence |  |  |  | 0
7.3.1 | Prepare Ground as per the structural drawing in readiness for hesco fence. | SM | 681.6 |  | 0
7.3.2 | Take stock, deliver to site and instal MIL7 8784 R with dimensions 87" (2.21m) height, and 84" (2.13m) wide single stacked for the internal hesco protection wall | LM | 320 |  | 0
7.3.3 | Provide sand or appropriate material to fill in the hesco sacks, ensuring that the fence is upright and evenly filled to avoid bulging | CM | 1506.336 |  | 0
| Total Carried to Summary |  |  |  | 0
7.4 | Razor Wire Fence
7.4.1 | Supply and place angle posts 50x50x6mm, 1.5 m high, anchored on top of the hesco using 100mm dia uPVC pipes class D placed inside the sand filling, 500mm deep and filled with class 15 concrete (1:3:6). The distance of the angle posts should be 1.5m apart to hold 980mm razor wire (measured seperately), and should be lagged at the bottom for anchorage. Allow for drilling 4 No. holes per angle post | No. | 215 |  | 0
7.4.2 | Supply and fix 12 Gauge 3mm strenghtening galvanised wire; 4 strands running through the angle posts for fastening razor wire (ms).The 12 Gauge galvanised wire should be tensioned so as have a minimum sag of 20mm from the horizontal. | Lm | 1280 |  | 0
7.4.3 | Provide all material and construct a single row of 980mm diameter heavy duty cross type concertina wire to be laid on top of existing HESCO barrier | Lm | 320 |  | 0
| Subtotal Element No.2- Barbed Wire Fencing |  |  |  | 0
SUMMARY
| BARBED WIRE |  |  |  | 0
| HESCO FENCE |  |  |  | 0
| RAZOR WIRE |  |  |  | 0
| TOTAL CARRIED TO MAIN SUMMARY |  |  |  | 0

## 8 WATCH TOWERS
ITEM | DESCRIPTION | UNIT | QNTY | RATE US$ | AMT US$
PROPOSED ……………………………………....
…….………………………………….. DISTRICT
8 | SECTION 8: WATCH TOWERS
SITE CLEARANCE
8.1 | Clear site of existing debris and cart away from
| the site as directed but not less than 100m | SM | 16
Carried to Collection
ELEMENT NO.2
EXCAVATION
8.2 | Excavate trench for foundation not exceeding
| 1.50 meters deep, starting from stripped levels | CM | 6
Disposal of excavated materials
8.3 | Cart away surplus excavated material | CM | 2
8.4 | Return fill and compact selected excavated materials around foundations | CM | 3
Carried to Collection
ITEM | DESCRIPTION | UNIT | QNTY | RATE US$ | AMT US$
ELEMENT NO.3
REINFORCED CONCRETE FRAME
Insitu concrete ; reinforced;class 20/(20mm): vibrated
8.5 | Construction of RCC beams of the floor and Collumn bases roof slab 0.2mx0.2mx8x2
| Assorted steel bars 4 No 12Ǿ at spacing of staff 200mm@Cc | CM | 1
8.6 | Construction of RCC columns with dimensions 0.4mx0.4mx7m
| Assorted steel bars for column footing both directions @ 16Ǿ spacing 200mm Cc | CM | 3
8.7 | RCC mat foundation trench and RCCA footings columns assorted steel bars for
| footing both directions 12diam specing 250mm@c-c | CM | 3
8.8 | Construction of RCC floor and roof slab for guard tower 2mx2mx0.2m
| steel bars of the floor& roof slab both X-direction | CM | 1
Reinforcement( all provisional)
Bars; high yield steel; cold worked to B.S. 4461 including
bends, hooks, tying wire and distance blocks
of assorted diameter
8.9 | Assorted bars | Kg | 200
In-situ concrete
Mass concrete( 1.3.6/38-38mm aggregate)
8.1 | 50mm thick mass concrete class Q(1:3:6) to bottoms of columns bases | SM | 2
Sawn formwork to insitu concrete as described:-
8.11 | to sides of suspended Slabs | SM | 16
8.12 | Ditto: sides of Columns bases | SM | 5
8.13 | Ditto: Beams | SM | 2.5
8.14 | To sides of the wall | SM | 6.5
8.15 | Toside of columns | SM | 40
Carried to Collection
ITEM | DESCRIPTION | UNIT | QNTY | RATE US$ | AMT US$
ELEMENT NO.4
WALLING
200mm thick reinforced concrete walling cast
cement and sand -aggregate (1:2:4) mortar, reinforcement with 12mm diam re bars
alternate course as described in:
8.16 | 200mm thick Reinforced concrete Retaining Wall
| at height of 1.4m class Q (1:3:6) at the top of Slab | MC | 1.68
8.17 | 8mm- 25 mm diameter assorted | KG | 150
Carried to Collection
ELEMENT NO.5
FINISHES
Wall finishes
Plaster; 12mm thick 2 No. coatwork, generally to: -
9mm first coat of cement sand (1:6); 3mm
second coat of cement and lime putty (1:10);
steel trowelled toconcrete or blockwork base
8.18 | Walls, and Columns | SM | 20
Painting and decorations
Prepare and apply three coats of first
quality silk vinyl paint to: -
8.19 | Plastered surfaces | SM | 20
Floor finishes
Beds or Backings
Screed; cement and sand (1:3)
8.2 | 40mm thick one coat backings; wood floated | SM | 4
to concrete base; smooth trowelled in red-oxide;
to floors level; internal
Carried to Collection
ITEM | DESCRIPTION | UNIT | QNTY | RATE US$ | AMT US$
ELEMENT NO.6
STEEL LADDER
8.21 | Supply and Provide 3m and 500mm wide Vertical
| ladder with railings on both sides to access | NO | 1
the Observation Post
Carried to Collection
ELEMENT NO.7
LIGHTING
8.22 | Supply all materials and mount 4 LED 150W floodlights
| on either side of the towers | No. | 4
Carried to Collection
MAIN SUMMARY
| ELEMENT No. |  | PAGE |  | AMOUNT
| 1 |  | 1/8
| 2 |  | 2/8
| 3 |  | 3/8
| 4 |  | 4/8
| 5 |  | 5/8
| 6 |  | 6/8
| 8 |  | 8/8
Total
Total for 4 No. Guard Towers

## 9 GATES
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE (US$) | AMOUNT (US$)
PROPOSED ……………………………………....
…….………………………………….. DISTRICT
9 | SECTION 9 : GATES
ELEMENT 1: SITE CLEARANCE
9.1 | Clear site of existing debris and cart away from
| the site as directed but not less than 100m | SM | 5 |  | 0
9.1 | Excavate trench for foundation not exceeding
| 1.50 meters deep, starting from stripped levels | CM | 5 |  | 0
9.2 | Extra over in rock excavation | Item | 1 |  | 0
Disposal of excavated materials
9.3 | Cart away surplus excavated material | CM | 5 |  | 0
Backfill
9.4 | Return fill and compact selected excavated materials
| around foundations | CM | 1.5 |  | 0
ELEMENT 3: REINFORCED CONCRETE FRAME
Plain concrete class 15 in:
9.5 | 100mm blinding | m2 | 0.25 |  | 0
9.6 | Ditto for column bases | m2 | 0.1 |  | 0
Insitu concrete class 25/20 , vibrated and reinforced with
60mm thick maximum aggregate size in as described, in:-
BEAMS
9.7 | Ground beam | m3 | 0.675 |  | 0
COLUMNS
9.8 | Columns bases | m3 | 0.6 |  | 0
9.9 | Starter columns | m3 | 0.32 |  | 0
9.1 | Columns (Height 2.7m) | m3 | 0.864 |  | 0
BEAMS
GROUND BEAM
9.11 | Y12 (Nominal Diameter 12mm) bars as main bars,
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 8.88 |  | 0
| Page Total Carried Forward |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE (US$) | AMOUNT (US$)
| Page Total Brought Forward |  |  |  | 0
9.12 | R8 (Nominal Diameter 8mm) bars as rings,
| Cross-Sectional Area (50.3mm2), Mass per unit length (0.395kg/m) | Kg | 8.69 |  | 0
COLUMNS
COLUMN BASES
9.13 | Y16 (Nominal Diameter 16mm) bars as main bars,
| Cross-Sectional Area (201mm2), Mass per unit length (1.579kg/m) | Kg | 21.4744 |  | 0
STARTER COLUMNS
9.14 | Y16 (Nominal Diameter 16mm) bars as main bars,
| Cross-Sectional Area (201mm2), Mass per unit length (1.579kg/m) | Kg | 18.948 |  | 0
9.15 | R8 (Nominal Diameter 8mm) bars as rings,
| Cross-Sectional Area (50.3mm2), Mass per unit length (0.395kg/m) | Kg | 8.3912 |  | 0
COLUMNS
6m HIGH COLUMNS
9.16 | Y16 (Nominal Diameter 16mm) bars as main bars,
| Cross-Sectional Area (201mm2), Mass per unit length (1.579kg/m) | Kg | 56.844 |  | 0
9.17 | R8 (Nominal Diameter 8mm) bars as rings,
| Cross-Sectional Area (50.3mm2), Mass per unit length (0.395kg/m) | Kg | 22.6562 |  | 0
Sawn formwork as described to:-
Beams
9.18 | To sides of ground beam | m2 | 4.5 |  | 0
ELEMENT 4: WALLING
SUBSTRUCTURE WALLING
Approved compacted rubble stone fill bedded and jointed in
cement sand mortar (1:4)
9.19 | 400mm thick rubble stone foundation walling | m3 | 2.4 |  | 0
ELEMENT 5: FINISHES
0
| Page Total Carried Forward |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE (US$) | AMOUNT (US$)
| Page total Brought forward |  |  |  | 0
Wall finishes
| Plaster; 12mm thick 2 No. coatwork, generally to: - |  |  |  | 0
9mm first coat of cement sand (1:6); 3mm
second coat of cement and lime putty (1:10);
steel trowelled to concrete or blockwork base
9.2 | Columns | m2 | 8.64 |  | 0
Prepare and apply three coats of first
quality silk vinyl paint to: -
9.21 | Columns | m2 | 8.64 |  | 0
ELEMENT 6: GATES
9.22 | Supply and fix double leaf steel gate size 5000x 2100mm high with
small pedestrian door made from 3mm thick steel plate welded on
both sides of the frame. Frame as follows: 75x50x3mm thick
RHS external members and 25mm SHS 3mm thick secondary
members, fixed onto the concrete columns using heavy duty steel
pin hinges; with all fastening accessories including all cutting welding,
grinding and priming with one coat of grey oxide before fixing.
The gate should also have peep holes of not more that 25mm dia
with a slilding door. It should also have 2 locking mechanisms,
| top and bottom. | No. | 1 |  | 0
SECTION 4: BOOM BARRIERS
ELEMENT NO.1
STEEL FRAME
9.23 | Supply and Provide 5'' (12.5cm) dia. Pipe for 9m long
with three layers that is bonded by 2'' (50mm) dia.
| Pipe as Per drawing. | LM | 69 |  | 0
9.24 | Supply and Provide C Section Steel strips for fastening
| the Steel Barrier. | LM | 14.4 |  | 0
9.25 | Supply and Provide Plate for filling mass Concrete to
| Balance the Steel Barrier. | SM | 2.5 |  | 0
MASS CONCRETE FRAME
9.26 | Fill the Box with Mass Concrete | MC | 0.343 |  | 0
FINISHES
9.27 | Allow a provisional sum for painting and
Transportation and inatallation work of
| the Steel Barriers on site | NO | 1 |  | 0
| TOTAL FOR 1NO. GATE AND BARRIER |  |  |  | 0
| TOTAL FOR 2 NO. GATES AND BARRIERS CARRIED TO MAIN SUMMARY |  |  |  | 0

## 10 SEPTIC TANK
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
GRANT No. ……………………………………….
PROPOSED ……………………………………....
11 | SECTION 10: SEPTIC TANK
Excavations including maintaining and supporting sides
and keeping free from water, mud and fallen material
11.1 | Stripping of surface and excavation for septic tank in soft soil up to depth of | C.M | 22.5 |  | 0
approximately 1.8m; pit dimensions: 32.5m width x 5m length
11.2 | Excavation for septic tank in hard rock at a depth approximately starting
at 1.8m, finishing at 3.0 m; 2.5m width x 5m length. (when rock is not
| encountered, the excavation rates in soft soil will apply at these depths) | C.M | 15 |  | 0
Reinforced concrete class 25,
11.3 | 150mm thick vibrated reinforced concrete for bottom | C.M | 1.88 |  | 0
slab (concrete class 20)
Reinforcement, as described (PROVISIONAL)
High yield square twisted reinforcement to BS 4461
11.4 | 10mm high tensile square twisted bars; cold worked; BS4461 | KG | 130 |  | 0
including bends, hooks, tying wire, distance blocks and spacers for bottom slab; Y10@ 200mm c/c
11.5 | Supply and fix sawn formwork to sides of bottom slab | L.M | 12.5 |  | 0
200x400mm block walling bedded and jointed in
cement and sand (1:4) mortar, reinforcement with and
including 25mm wide x 20 gauge hoop iron at every
alternate course as described in:
| Page Total Carried Forward |  |  |  | 0
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
| Page Total Brought Forward |  |  |  | 0
11.6 | Sub-Structure walling | S.M | 43.75 |  | 0
Cement and sand (1:3) screeds, backings, beds etc
11.7 | 15mm thick two coat cement sand (1:3) plaster trowelled smooth and | S.M | 62.5 |  | 0
comprising 12mm backing and 3mm finishing coat for internal walls.
Reinforced concrete class 20,
11.8 | Supply all materials and cast a 125mm thick vibrated reinforced | C.M | 1.6 |  | 0
concrete slab, mix1:2:4 or class 20/20. Top slab dimensions 2.5m x 5.0m
Reinforcement, as described (PROVISIONAL)
High yield square twisted reinforcement to BS 4461
11.9 | 10mm high tensile square twisted bars; cold worked; BS4461 | KG | 130 |  | 0
including bends, hooks, tying wire, distance blocks and spacers for
top slab; Y10@ 200mm c/c .
11.1 | Supply and fix sawn formwork to sides of bottom slab | L.M | 12.5 |  | 0
11.11 | Supply and fix sawn formwork beneath the slab | S.M | 12.5 |  | 0
11.12 | Manhole walling; 800mm wide x 800mm long x 450mm depth | S.M | 3 |  | 0
11.13 | Manhole frame and covers | Pcs. | 4 |  | 0
11.14 | Tank piping, fittings and accessories which includes among others | Item | 1 |  | 0
ring bearers anchored in the wall and a 2.5 m heigh 4'' vent pipe
with rain cower and fly net
| Page Total Carried Forward |  |  |  | 0
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
| Page Total Brought Forward |  |  |  | 0
11.15 | 4" brown sewer pipes with accessories laid with 1% slope in trench | L.M | 12 |  | 0
of 0.5 to 0.8 m depth
Reinforced concrete class 25,
11.16 | Supply all materials and cast R.C. buffer beam, 100mm wide x 450mm deep, | C.M | 0.3 |  | 0
concrete class 20
11.17 | 12mm high tensile square twisted bars; cold worked; BS4461 including | KG | 22 |  | 0
bends, hooks, tying wire, distance blocks and spacers for ring beam
reinforcement, 4Y12
11.18 | Curing of all concrete and masonry works. Where applicable, | Item | 1 |  | 0
sand may be used for covering the concrete or masonry works to be
cured and removed afterwards.
ELEMENT 2 : SOAK PIT
11.19 | Excavate 1.5m diameter x 3.5m depth pit | C.M | 5.5 |  | 0
11.2 | Backfill with well packed approved hardcore to 2m depth | C.M | 3.5 |  | 0
11.21 | Plastic sheeting | S.M | 2 |  | 0
11.22 | 200mm thick normal soil backfill | C.M | 0.4 |  | 0
| SEPTIC TANK TOTAL CARRIED TO MAIN SUMMARY |  |  |  | 0

## 11 GENERATOR SHED and instal
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
GRANT No. ……………………………………….
PROPOSED ……………………………………....
11 | SECTION 11: GENERATOR HOUSE
SITE PREPARATION
11.1 | Clear site of all trees, bushes and shrubs, grab up roots and
burn the arisings.
11.2 | Load, wheel and cart deposit and spread surplus excavated
material where directed on site at a distance not exceeding
| 100 meters | LS | 1 |  | 0
SUBSTRUCTURES (PROVISIONAL)
Excavations including maintaining and supporting sides
and keeping free from water, mud and fallen material
11.3 | Excavate trench for foundation not exceeding 1.50 meters
| deep, starting from stripped levels | CM | 14.4 |  | 0
Disposal
11.4 | Return, fill and ram selected excavated material around
| foundations | CM | 9.6 |  | 0
11.5 | Load, wheel and cart deposit and spread surplus excavated
material where directed on site at a distance not exceeding
| 100 meters | CM | 4.8 |  | 0
Hardcore or other approved filling, as described
11.6 | 300mm thick well compacted hardcore filling blinded with
| 25mm thick quarry dust layer to receive surface bed | SM | 37 |  | 0
Anti-termite treatment
11.7 | Gladiator or equal and approved chemical anti-termite
treatment, executed complete by an approved specialist
| under a ten-year guarantee, to surfaces of hard-core | SM | 37 |  | 0
| Page Total Carried Forward |  |  |  | 0
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
| brOUGHT Forwaard from Previous Page |  |  |  | 0
Damp-proof membrane
11.8 | 1000 gauge polythene or other equal and approved damp-proof membrane, laid over blinded hardcore (m.s) with 300mm side and end laps (measured nett-allow for laps) | SM | 37 |  | 0
Plain concrete class 15 in:
11.9 | 50mm blinding under strip footing | SM | 14.4 |  | 0
Reinforced concrete class (20) as described, in:-
11.1 | Strip footing | CM | 2.88 |  | 0
11.11 | Lintols | CM | 0.069 |  | 0
11.12 | 125mm thick surface bed laid in bays including all
| necessary formwork | CM | 3 |  | 0
11.13 | Ditto for generator plinths | CM | 0.72 |  | 0
Reinforcement, as described:-[PROVISIONAL]
High yield square twisted reinforcement bars to B.S 4461
FOOTING
11.14 | 8mm bars | Kg | 44.424 |  | 0
11.15 | 10mm bars | Kg | 26.544 |  | 0
LINTOLS
11.16 | 8mm bars | Kg | 3.702 |  | 0
11.17 | 10mm bars | Kg | 2.212 |  | 0
Mesh fabric reinforcement to B.S 4483 and setting in
concrete with 300mm side and end laps
(measured nett-allow for laps).
11.18 | Fabric ref. A142 weighing 2.22kg/ sq.metre, in surface
| bed | SM | 32 |  | 0
11.19 | Ditto for ramp | SM | 7 |  | 0
| Page Total Carried Forward |  |  |  | 0
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
| Page Toal Brought Forward |  |  |  | 0
Sawn formwork as described to:-
11.2 | To edge of steps and slabs over 75mm but not exceeding
| 150mm high | LM | 24 |  | 0
11.21 | Sides and soffits of lintols | LM | 2 |  | 0
ELEMENT NO. 3
WALLING
200x400mm hollow block walling bedded and jointed in cement and sand (1:4) mortar, reinforcement with and including 25mm wide x 20 gauge hoop iron at every alternate course as described in:
11.22 | 200mm thick walling Sub-structure walling | SM | 19.2 |  | 0
11.23 | 200mm thick walling Super-structure walling | SM | 27 |  | 0
11.24 | Ditto for dwarf wall | SM | 10.4 |  | 0
Damp-proof courses, as described, to walls
11.25 | 200mm wide | LM | 37.4 |  | 0
11.26 | 100mm dia. Galvanized Circular Hollow Section (CHS)poles | No. | 4 |  | 0
11.27 | Heavy duty fabric mesh | SM | 26 |  | 0
11.28 | 150x50mm timber framework | LM | 48 |  | 0
ELEMENT NO. 4
ROOF CONSTRUCTION AND FINISHES
The following in sawn cellcured timber roof trusses with nailed
connections including hoisting and fixing in position
11.29 | 100x50mm rafters | LM | 60 |  | 0
11.3 | 100x50mm strut or tie | LM | 30 |  | 0
| Page Total Carried Forward |  |  |  | 0
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
| Page Total Brought Forward |  |  |  | 0
11.31 | 100x50mm tie beam | LM | 35 |  | 0
11.32 | 100x50mm wall plate fixed with and including 200mm
| long 12mm diameter rag bolts cast into beam at 1500mm centres galvanised | LM | 24 |  | 0
Roof sheets as IT4 profile gauge 28 pre-painted galvanised
11.34 | Roof sheets as IT4 profile gauge 28 pre-painted galvanised laps hook bolts, PVC washer and tropicalized slip cup | SM | 38 |  | 0
ELEMENT NO. 5
FINISHES
15 mm cement and sand (1:3) render, finished with
woodfloat to:-
11.35 | Concrete or masonry surfaces internally and externally | SM | 37.4 |  | 0
12mm (minimum) two coat lime plaster as described to
11.36 | Concrete or masonry surfaces internally | SM | 37.4 |  | 0
Floor Finishes
Cement and sand (1:3) screeds, backings, beds etc
11.37 | 40mm bed finished floor screed | SM | 32 |  | 0
Painting and decorating
Prepare and apply three coats first quality emulsion
paint on:-
11.38 | Plastered walls externally | SM | 37.4 |  | 0
Prepare and apply three coats first quality silk vinyl
emulsion paint on:-
11.39 | Plastered surfaces internally | SM | 37.4 |  | 0
| Page Total Carried Forward |  |  |  | 0
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
| Page Total Brought Forward |  |  |  | 0
ELEMENT NO. 6
DOORS
Purpose built steel door complete with heavy gauge
mesh on 2" diameter galvanized iron framework.
framework including cutting handling, hoisting fixing in position
at all heights with all necessary ironmongery and
applying a priming coat of approved steel primer.
11.4 | Double door overall size 2800x2700mm high | No. | 1 |  | 0
double leaf
11.41 | Single door overall size 900x2100mm high
| single leaf | No. | 1 |  | 0
Allow for PCC vents
11.42 | 2000X1000mm high | LS | 1 |  | 0
SECTION 4: GENERATOR INSTALLATION
ELEMENT No. 1 : GENERATOR
30KVA TIER 3 PRIME RATED SOUND
ATTENUATED DIESEL GENERATOR INSTALLATION
11.44 | Supply sound attenuated 45kVA, 415V 50Hz prime rated tier 3 diesel engine generator set with water cooled Perkins, SDMO or Cummins engine complete with TP Automatic Mains Failure panel with integral synchronization control module, 8 hour base fuel tank, 250A TP output circuit breaker. | No. | 1 |  | 0
| Page Total Carrie Forward |  |  |  | 0
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
| Page Total Brought Forward |  |  |  | 0
ELEMENT No. 2 : GENERATOR INSTALLATION
Install, test and commission as per BS 7671:2001
the following as described below: All materials and
equipment are supplied by the client except for the
miscellaneous items expressly stated to be supplied
by contractor or as directed by the client's representative.
11.45 | Allow for fixing of gen set to floor slab as recommended by the Manufacturer complete with anti vibration mountings. The contractor to provide duct or trench for all cable entry from the generator and to the main LV switchboard and Reconstruct the Floor in Concrete 1:2:4 ratio and their Finishing. | No. | 1
ELEMENT No. 3 : ELECTRICAL SUPPLY
Trench excavation
11.46 | Excavate trench 300mm width 500mm depth from ground level from the generator room to main building approx. | m | 200
Cabling
11.47 | Supply, install and connect 1x3x95+1x50 Sq. mm
SC XLPE/SWA/PVC Copper cable from Generator to
| LV Switchboard and complete with cable lags and glands | m | 200
ELEMENT No. 4 : ACCESSORIES
11.48 | Change Over 4 Pole 225 A | Pc(s) | 2
11.48 | Cable 4X35 mmsq | M | 20
11.48 | Grounding Bar | Pc(s) | 4
11.48 | Grounding Cable 1X16 mm sq | Roll | 3
11.48 | Main Switch 4 Pole 200 A | Pc(s) | 1
11.48 | Distribution Panel(DP) 12 Breakers | Pc(s) | 1
11.48 | Tube Chanel 50X50 MM | Pc(s) | 12
11.48 | PVC Pipe 0.6x0.6m | Pc(s) | 12
11.48 | Concrete Nail | Box | 4
11.48 | Insulating Tape | Pc(s) | 10
11.48 | Exhaust Pipes | M | 9
11.48 | Battery Acid | Litre | 20
11.48 | Miscellenous | LS | 1
11.48 | Allow for the supply and installation of labels and danger warning notices | LS | 1
| GENERATOR SHED AND INSTALLATION CARRIED OT MAIN SUMMARY |  |  |  | 0

## 12 WATER STORAGE TANKS
ITEM | DESCRIPTION | UNIT | QNTY | RATE | AMT US$
PROPOSED ……………………………………....
…….………………………………….. DISTRICT
12 | SECTION 12: WATER TOWER
12.1 | Site Clearance
12.2 | Clear site of all bushes and debris. Grab up roots and | m2 | 30 |  | 0
| burn the arisings |  |  |  | 0
0
12.3 | Load, wheel and cart deposit and spread surplus excavated material where directed on site at a distance not exceeding 100 meters | Item | 1
| Total carried to summary | $
12.4 | ELEMENT NO. 2 : SUBSTRUCTURES (PROVISIONAL)
12.5 | Excavations including maintaining and supporting sides
and keeping free from water, mud and fallen material
12.6 | Top soil excavation average 200mm deep | m3 | 6 |  | 0
0
12.7 | Excavate for foundation not exceeding 0.3 |  |  |  | 0
| meters deep, starting from stripped levels | m3 | 0.6 |  | 0
0
12.8 | Extra over for excavation in rock | m3 | 3 |  | 0
0
12.9 | Ditto Column bases | m3 | 30 |  | 0
0
| Planking and strutting |  |  |  | 0
0
12.1 | Allow for keeping foundations free from water, mud, fallen |  |  |  | 0
| materials, etc. | LS | 1 |  | 0
0
| Disposal |  |  |  | 0
0
12.11 | Return, fill and ram selected excavated material around |  |  |  | 0
| foundations | m3 | 9 |  | 0
0
12.12 | Load, wheel and cart deposit and spread surplus |  |  |  | 0
| excavated material where directed on site at a |  |  |  | 0
| distance not exceeding 100 meters | m3 | 21 |  | 0
| Page Total Carried Forward |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QNTY | RATE | AMT US$
| Total Brought forward |  |  |  | 0
Hardcore or other approved filling, as described
12.13 | 300mm thick well compacted hardcore filling blinded with
| 25mm thick quarry dust layer to receive surface bed | m2 | 1.8 |  | 0
0
12.14 | 50mm thick Quarry dust blinding to surfaces of hardcore :rolled | m2 | 20 |  | 0
| smooth to receive polytheen sheeting (m.s) |  |  |  | 0
0
| Anti-termite treatment |  |  |  | 0
0
12.15 | Gladiator or equal and approved chemical anti-termite |  |  |  | 0
| treatment, executed complete by an approved specialist |  |  |  | 0
| under a ten-year guarantee, to surfaces of blinding | m2 | 20 |  | 0
0
| Damp-proof membrane |  |  |  | 0
0
12.16 | 1000 gauge polythene or other equal and approved |  |  |  | 0
| damp-proof membrane, laid over blinded hardcore |  |  |  | 0
| (m.s) with 300mm side and end laps (measured |  |  |  | 0
| nett-allow for laps) | m2 | 20 |  | 0
0
ELEMENT NO. 3 : CONCRETE WORKS
Plain concrete class 15 in:
12.17 | 100mm blinding | m3 | 2
12.18 | Ditto for column bases | m3 | 0.6
12.19 | Insitu concrete class 25/20 , vibrated and reinforced with 60mm thick
maximum aggregate size in as described, in:-
BEAMS
12.2 | Ground beam | m3 | 5.67 |  | 0
0
12.21 | Ring beam 1 | m3 | 5.67 |  | 0
0
12.22 | Ring beam 2 | m3 | 5.67 |  | 0
0
| Page Total Carried Forward |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QNTY | RATE | AMT US$
Page Total Forward Forward
| COLUMNS |  |  |  | 0
0
12.23 | Columns bases | m3 | 3.6 |  | 0
0
12.24 | Starter columns | m3 | 2.16 |  | 0
0
12.25 | Columns (Height 6m) | m3 | 12.96 |  | 0
0
| SLABS |  |  |  | 0
0
12.26 | 200mm thick surface bed laid in bays including all |  |  |  | 0
| necessary formwork | m3 | 4 |  | 0
0
| Ditto: |  |  |  | 0
0
12.27 | Suspended slab | m3 | 4 |  | 0
0
12.28 | Roof slab | m3 | 4 |  | 0
0
| Reinforcement, as described:-[PROVISIONAL] |  |  |  | 0
0
12.29 | High yield square twisted reinforcement bars to B.S 4461 including cutting bending and tying |  |  |  | 0
BEAMS
GROUND BEAM
12.3 | Y12 (Nominal Diameter 12mm) bars as main bars,
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 125 |  | 0
0
12.31 | R8 (Nominal Diameter 8mm) bars as rings, |  |  |  | 0
| Cross-Sectional Area (50.3mm2), Mass per unit length (0.395kg/m) | Kg | 41 |  | 0
0
| RING BEAM 1 |  |  |  | 0
0
12.32 | Ditto for Y12 as main bars | Kg | 125 |  | 0
0
| RING BEAM 2 |  |  |  | 0
12.33 | Ditto for Y12 as main bars | Kg | 125 |  | 0
0
12.34 | Ditto for R8 as rings | Kg | 41 |  | 0
| Page Total Carried Forward |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QNTY | RATE | AMT US$
| Page Total Brought Forward |  |  |  | 0
12.35 | Ditto for R8 as rings | Kg | 41 |  | 0
0
| COLUMNS |  |  |  | 0
0
| COLUMN BASES |  |  |  | 0
0
12.36 | Y16 (Nominal Diameter 16mm) bars as main bars, |  |  |  | 0
| Cross-Sectional Area (201mm2), Mass per unit length (1.579kg/m) | Kg | 65 |  | 0
0
| STARTER COLUMNS |  |  |  | 0
12.37 | Y16 (Nominal Diameter 16mm) bars as main bars, |  |  |  | 0
| Cross-Sectional Area (201mm2), Mass per unit length (1.579kg/m) | Kg | 57 |  | 0
0
12.38 | R8 (Nominal Diameter 8mm) bars as rings, |  |  |  | 0
| Cross-Sectional Area (50.3mm2), Mass per unit length (0.395kg/m) | Kg | 25 |  | 0
0
6m HIGH COLUMNS
12.39 | Y16 (Nominal Diameter 16mm) bars as main bars,
| Cross-Sectional Area (201mm2), Mass per unit length (1.579kg/m) | Kg | 171 |  | 0
0
12.4 | R8 (Nominal Diameter 8mm) bars as rings, |  |  |  | 0
| Cross-Sectional Area (50.3mm2), Mass per unit length (0.395kg/m) | Kg | 151 |  | 0
0
| ROOF SLAB |  |  |  | 0
12.41 | Y12 (Nominal Diameter 12mm) bars as main bars tops 1 |  |  |  | 0
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 71 |  | 0
0
12.42 | Y12 (Nominal Diameter 12mm) bars as main bars tops 2 |  |  |  | 0
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 71 |  | 0
0
12.43 | Y12 (Nominal Diameter 12mm) bars as main bars bottom 1 Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 71 |  | 0
0
12.44 | Y12 (Nominal Diameter 12mm) bars as main bars bottom 2 Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 71
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QNTY | RATE | AMT US$
PAGE TOTA L BROUGH FORWARD
0
| BASE SLAB |  |  |  | 0
12.45 | Y12 (Nominal Diameter 12mm) bars as main bars tops 1 |  |  |  | 0
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 71 |  | 0
0
12.46 | Y12 (Nominal Diameter 12mm) bars as main bars tops 2 |  |  |  | 0
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 71 |  | 0
0
12.47 | Y12 (Nominal Diameter 12mm) bars as main bars bottom 1Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 71 |  | 0
0
12.48 | Y12 (Nominal Diameter 12mm) bars as main bars bottom 2 |  |  |  | 0
0
12.49 | Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 71 |  | 0
| WALLS |  |  |  | 0
0
12.5 | Y12 (Nominal Diameter 12mm) bars as main bars tops 1 |  |  |  | 0
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 153.4464
12.51 | Y12 (Nominal Diameter 12mm) bars as main bars tops 2
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) | Kg | 153.4464
Reference A142 mesh 200 x 200 mm , weight 2.22 kgs per
square meter ( measured net - no allowance made for laps
(inclunding bends, tying wire and distance blocks)
12.52 | Fabric ref. A142 weighing 2.22kg/ sq.metre, in surface
| bed | m2 | 20
Sawn formwork as described to:-
12.53 | To edge of floor slab | m2 | 3.6
12.54 | Ditto to sides and soffits of roof slab | m2 | 8
| PAGE TOTAL CARRIED FORWARD | $
ITEM | DESCRIPTION | UNIT | QNTY | RATE US$ | AMT US$
| PAGE TOTAL BROUGHT FORWARD |  |  |  | 0
12.55 | Ditto to sides and soffits of base slab | m2 | 8
12.56 | Ditto to walls | m2 | 43.2
SUPER-STRUCTURE WALLING
12.57 | Insitu concrete class 25/20 , vibrated and reinforced with 60mm thick
maximum aggregate size in as described, in:-
12.58 | 200 mm thick reinforced wall | m3 | 8.64
ELEMENT NO. 6 : FINISHES
Cement and sand (1:3) screeds, backings, beds etc
25mm Thick cement/sand (1:4) screed finish
12.59 | Floor slab | m2 | 20
15 mm cement and sand (1:3) render, finished with
wood float to:-
12.6 | Concrete or masonry surfaces externally
12.61 | Outside roof slab | m2 | 20
12.62 | Ditto outside base slab | m2 | 20
12.63 | Ditto Outside walls | m2 | 54
12.64 | Ditto for columns | m2 | 86.4
Lightweight water proofed screeds and plaster
15 mm cement and sand (1:3) render, finished with
steel float to:-
12.65 | Concrete or masonry surfaces internally
12.66 | Inside roof top slab | m2 | 20
12.67 | Ditto inside base slab | m2 | 20
12.68 | Ditto inside walls | m2 | 54
| PAGE TOTAL CARRIED FORWARD | $
ITEM | DESCRIPTION | UNIT | QNTY | RATE US$ | AMT US$
| PAGE TOTAL BROUGHT FORWARD |  |  |  | 0
Painting
Fill uneven surfaces with stucco filler to approval and apply two coats soft white external textured paint to:
12.69 | Plastered and rendered surfaces | m2 | 180.4
Prepare surfaces and apply three coats gloss oil paint as 'Crown' or equal and approved manufacturer(s) on concrete and masonry surfaces: measured overall on both sides
12.7 | Plastered surfaces internally and externally | m2 | 180.4
ELEMENT NO. 7 : PLUMBING INSTALLATIONS
12.71 | Galvanized Mild Steel pipes class "B" medium thickness with and
including jointing, fittings and fixe as described
12.72 | Supply and install 50mm diameter inlet pipe 800mm long | No. | 1
12.73 | Supply and install 50mm diameter draw off pipe Ditto | No. | 1
12.74 | Supply and install 50mm diameter overflow pipe Ditto | No. | 1
12.75 | Supply and install 75mm diameter scour pipe Ditto | No. | 1
12.76 | Supply and install 20mm diameter brass gate valve with wheel and head | No. | 1
12.77 | Supply and install 20mm diameter stop corks | No. | 1
12.78 | Supply and install 600x600x6mm heavy gauge steel primed metal manhole cover on slab with and including metal framing all around | No. | 1
12.79 | Supply and install 20mm Diameter bars, ‘U’ shaped to form steps with ends embedded into retaining wall, average length 450mm | No. | 1
TOTAL CARRIED TO GRAND SUMMARY

## 13STREET LIGHTS
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (US$) | AMOUNT (US$)
SECTION 13: SOLAR STREETLIGHTS
PROPOSED STREETLIGHT INSTALLATION
KISIMAYO FEMALE TRANSITION CENTRE
ELEMENT NO. 1
Solar Streetlights
13.1 | Supply solar panel lights packed with battery, | No | 10 |  | 0
light source socket, controller that regulates batteries
and has a low voltage disconnect, light fixture, light fixture
mounting bracket, battery box, and the entire solar lighting
mounted to a pole, together with the accessories, cables, etc.
13.2 | Assemble solar panel lights packed with battery, | No | 10 |  | 0
light source socket, controller that regulates batteries
and has a low voltage disconnect, light fixture, light fixture
mounting bracket, battery box, and the entire solar lighting
mounted to a pole, together with the accessories, cables, etc.
13.3 | Fix or install solar panel lights packed with battery, | No | 10 |  | 0
light source socket, controller that regulates batteries
and has a low voltage disconnect, light fixture, light fixture
mounting bracket, battery box, and the entire solar lighting
mounted to a pole, together with the accessories, cables, etc.
| TOTAL CARRIED TO MAIN SUMMARY | US$ |  |  | 0

## 14Children Play area
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL
GRANT No. ……………………………………….
PROPOSED ……………………………………....
…….………………………………….. DISTRICT
14 | SECTION 14 : CHILDREN PLAY AREA
14.1 | Clear site of all bushes and debris. Grab up roots and | sm | 350 |  | 0
| burn the arisings |  |  |  | 0
0
14.2 | Supply and fix round timber posts minimum diameter 150mm 4m long, 1m fixed into the ground in a mass concrete footing 450*450mm*1 m deep including excavation and disposal of excavated material. | no. | 15 |  | 0
0
| ELEMENT NO. 4 : ROOFING |  |  |  | 0
| ROOF COVERING AND RAINWATER DISPOSAL |  |  |  | -
-
| Roof covering |  |  |  | -
14.3 | 28 gauge pre painted IT4 box profile iron sheets on timber structure (ms) | SM | 470 |  | 0
14.4 | Ridge or hip cap, 28 gauge prepainted | LM | 20 |  | 0
Structural Timbers
SAWN TREATED CYPRESS, Grade S50, pressure
impregnated
14.5 | 150 x 50 mm as trusses and rafters | LM | 150 |  | 0
14.6 | 100 x 50 mm as trusses, trussed joists and struts | LM | 975 |  | 0
14.7 | 75x50mm purlins and joists and struts | LM | 500 |  | 0
14.8 | 150 x 50 mm as King post | LM | 25 |  | 0
14.9 | Ditto, wall plate | LM | 75 |  | 0
14.1 | 25 x 150mm splice plates | LM | 15 |  | 0
14.11 | 25 x 200mm Ridge board | LM | 85 |  | 0
14.12 | 100 × 100 × 100 × 3mm thick angle cleat nailed to timber | NO | 15 |  | 0
Boarding
14.13 | 25 x 250 mm Fascia board fixed to rafters | LM | 85 |  | 0
Painting and decorating
14.14 | Ditto but 3 coats gloss oil paint to fascia board 200-300mm girth | LM | 85 |  | 0
| ROOFING TOTAL CARRIED TO MAIN SUMMARY |  |  |  | 0

## 15 STAFF TOILET
15 | SECTION 15: STAFF TOILET
ELEMENT NO. 1 : SITE PREPARATION
15.1 | Clear site of all bushes and debris. Grab up roots and | m2 | 11.89 |  | 0
burn the arisings
15.2 | Load, wheel and cart deposit and spread surplus excavated material where directed on site at a distance not exceeding 100 meters | Item | 1 |  | 0
15.3 | ELEMENT NO. 2 : SUBSTRUCTURES (PROVISIONAL)
Excavations including maintaining and supporting sides and keeping free from water, mud and fallen material
15.4 | Top soil excavation average 200mm deep | m2 | 11.89 |  | 0
15.5 | Excavate trench for foundation not exceeding 1.50
| meters deep, starting from stripped levels | m3 | 16 |  | 0
Planking and strutting
15.6 | Allow for keeping foundations free from water, mud, fallen materials, etc. | LS | 1
Disposal
15.7 | Return, fill and ram selected excavated material around foundations | m3 | 16
15.8 | Load, wheel and cart deposit and spread surplus
excavated material where directed on site at a
| distance not exceeding 100 meters | m3 | 16 |  | 0
Hardcore or other approved filling, as described
15.9 | 300mm thick well compacted hardcore filling blinded with 25mm thick quarry dust layer to receive surface bed | m2 | 4.756 |  | 0
15.1 | 50mm thick Quarry dust blinding to surfaces of hardcore :rolled smooth to receive polytheen sheeting (m.s) | m2 | 0.5945 |  | 0
Anti-termite treatment
15.11 | Gladiator or equal and approved chemical anti-termite treatment, executed complete by an approved specialist under a ten-year guarantee, to surfaces of blindinG | m2 | 4.756
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QNTY | RATE | AMT US$
PAGE TOTAL BROUGHT FORWARD
Damp-proof membrane
15.12 | 1000 gauge polythene or other equal and approved
damp-proof membrane, laid over blinded hardcore
(m.s) with 300mm side and end laps (measured
| nett-allow for laps) | m2 | 4.756 |  | 0
Reference A142 mesh 200 x 200 mm , weight 2.22 kgs per square meter ( measured net - no allowance made for laps (inclunding bends, tying wire and distance blocks)
15.13 | Fabric ref. A142 weighing 2.22kg/ sq.metre, in surface
| bed | m2 | 4.756 |  | 0
ELEMENT NO. 3 : CONCRETE WORKS
Plain concrete class 15 in:
15.14 | 50mm blinding | m2 | 9.6 |  | 0
Insitu concrete class 25/20 , vibrated and reinforced as described, in:-
15.15 | Beams | m3 | 1.5 |  | 0
15.16 | 200mm thick surface bed laid in bays including all
| necessary formwork | m3 | 1.7 |  | 0
Reinforcement, as described:-[PROVISIONAL]
High yield square twisted reinforcement bars to B.S 4461
BEAMS
15.17 | Ditto for Y12 as main bars | Kg | 85.248 |  | 0
15.18 | Ditto for R8 as rings | Kg | 67.1296 |  | 0
Sawn formwork as described to:-
15.19 | To edge of floor slab | m2 | 3.2 |  | 0
15.19 | Ditto to sides and soffits of roof slab | m2 | 23.66 |  | 0
15.2 | Ditto to sides of steps | m2 | 19.2 |  | 0
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QNTY | RATE | AMT US$
PAGE TOTAL BROUGHT FORWARD
15.21 | ELEMENT NO. 4 : WALLING
SUB-STRUCTURE WALLING
Approved compacted hardcore fill bedded and jointed in
cement sand mortar (1:4)
15.22 | 400mm thick rubble stone foundation walling | m3 | 9.6 |  | 0
SUPER-STRUCTURE WALLING
200x400mm hollow block walling bedded and jointed in cement and sand (1:4) mortar, reinforcement with and ncluding 25mm wide x 20 gauge hoop iron at every alternate course as described in
15.23 | 200 mm thick reinforced in every third course | m2 | 48 |  | 0
Horizontal Damp Proof Course:one layer of 3-ply bituminous felt or other equal approved (measured nett-allow for laps)
15.24 | 200mm wide; B.S. 743 Type A bitumen hessian base 150 mm laps (no allowance made for laps); horizontal, 1 no. layer, bedded in cement sand (1:3) mortar: | LM | 16
15.25 | PCC coping above parapet wall | LM | 16 |  | 0
15.26 | Supply and install heavy duty PPR pipes including all connections | LS | 1 |  | 0
SANITARY INSTALLATIONS
Sanitary appliances complete with all the connections to services, waste, jointing to supply overflows and plugging and screwing to the floors. Where trade names are mentioned below, the reference is intended to be as a guide to the type of fitting.
15.27 | Pedestal wash hand basin in white vitreous china size 500x400 mm complete with 'Aztec' chromed taps and handles, a 32mm diameter chrome plated pop-up waste and a 32mm Caradon Terrain' plastic bottle trap. Wash hand basin to be as 'Twyford Galerie Design' or equal and approved | No. | 2 |  | 0
| Page Total Carried Forward |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QTY |  | TOTAL
| Page Total brought Forward |  |  |  | 0
Water closet (W.C.) suite in white vitreous china comprising:
Glazed W.C. pan with heavy duty unbreakable plastic seat and cover,
close couple cistern and fittings, 6.0 litres, including chrome lever and
cover clip and WC outlet connector. The cistern to have internal overflow.
15.28 | Water closet pan to be as 'Twyford classic' or equal and approved | No. | 4 |  | 0
15.29
Recessed toilet roll holder in white vitreous china size 150x150 mm.
15.3 | To be as 'Twyford' or equal and approved | No. | 4 |  | 0
Wall-mounted push-button soap dispenser complete with initial charge
and mounting brackets. Soap dispenser to be as 'Star mix' or equal
15.31 | and approved | No. | 2 |  | 0
6 mm thick polished beveled plate glass mirror size 610x610 mm on
foam and 6 mm plywood timber backing in hard wood timber framing
15.32 | fixed on wall with dome headed brass screws | No. | 2 |  | 0
Allow for all all connections, pressure testing at 4 bars for 24hours and
commissioning of the sanitary fittings and accessories to the entire
15.33 | satisfaction of the Engineer. | LS | 1 |  | 0
0
| PLUMBING TOTAL CARRIED TO MAIN SUMMARY |  |  |  | 0
s
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QNTY | RATE | AMT US$
PAGE TOTAL BROUGHT FORWARD
ELEMENT NO. 5 : ROOF FINISHES
6.5 | ROOF COVERING AND RAINWATER DISPOSAL
(PROVISIONAL)
Roof covering
6.5.1 | 28 gauge pre painted galvanized corrugated iron sheets on timber structure (ms) | SM | 12
6.5.2 | Ridge or hip cap, 28 gauge prepainted | LM | 4.1
Structural Timbers
SAWN TREATED CYPRESS, Grade S50, pressure
impregnated (Provisional)
6.5.3 | 100 x 50 mm as trussed rafters, joists and struts | LM | 16
6.5.4 | 75x50mm purlins | LM | 31
6.5.5 | 100x50 mm Hip rafters | LM | 8.2
6.5.6 | Ditto, wall plate | LM | 8.2
6.5.7 | 25 x 150mm splice plates | LM | 8.2
6.5.8 | 25 x 200mm Ridge board | LM | 8.2
6.5.9 | Mild steel
6.5.10 | 100 × 100 × 100 × 3mm thick angle cleat nailed to timber | NO | 6
Boarding
6.5.11 | WROT CYPRESS, Prime Grade
6.5.13 | 32 x 250 mm Fascia board fixed to rafters | LM | 9
Painting and decorating
6.5.15 | Ditto but 3 coats gloss oil paint to fascia board 100-200mm girth | LM | 9
4.69 | Timber fascia 200-300mm girth | LM | 9
| Total carried to summary | $
PAGE TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QNTY | RATE | AMT US$
PAGE TOTAL BROUGHT FORWARD
6.6 | ELEMENT NO. 6 : FINISHES
Floor Finishes
Cement and sand (1:3) screeds, backings, beds etc
6.6.1 | 25mm Thick cement/sand (1:4) screed to steel trowelled finish | m2 | 11.89 |  | 0
6.6.3 | Skirtings;
100mm wide with rounded junction with wall finish and coved junction
| with floor finish | m2 | 1.2 |  | 0
6.6.4 | Ditto for edge of steps and slab | m2 | 19.2 |  | 0
Wall Finish
15 mm cement and sand (1:3) render, finished with
woodfloat to:-
6.6.5 | Concrete or masonry surfaces internally and externally
| Painting | m2 | 48 |  | 0
Fill uneven surfaces with stucco filler to approval and apply two coats soft white external textured paint to:
6.6.6 | Plastered and rendered surfaces | m2 | 48 |  | 0
Prepare and apply two undercoats of brilliant white emulsion paint
(RAL Code 9001) and two finishing coats of first quality brilliant white
Silk Vinyl emulsion paint (RAL Code 9001) to;-
6.6.7 | Plastered surfaces internally and externally | m2 | 48 |  | 0
6.6.8 | Vent grills | LS | 1 |  | 0
| Total carried to Main summary | $ |  |  | 0
ITEM | DESCRIPTION | UNIT | QNTY |  | AMT US$
ELEMENT NO. 7 : ELECTRICAL INSTALLATIONS
Lighting Fittings
6.7.1 | Supply and install following lighting fixtures with all accessories as per the specifications and drawings and complete with lamp fitting and accessories of Engineer or approved make.
6.7.2 | Type 4S - 4x18w surface mount flourescent light fitting | No. | 2 |  | 0
6.7.3 | Type W1 - 1x36w Surface mounted waterproof polycarbonate flourescent light fitting | No. | 1 |  | 0
Switches
6.7.4 | 5 Amps two gang one way switch | No | 1 |  | 0
Socket outlets
Supply and installation of fused shuttered switched socket outlet to comply with relevant BS standard (Clipsal, Orange, Crabtree/ Tenby/ABB or equivalent). Wiring (including supply of earth wire and all other material required) of above socket outlet using approved type 2.5mm² PVC/PVC copper cable and 2.5mm² earth wire drawn through securely fixed concealed PVC conduit in a ring circuit.
Socket outlet points
6.7.5 | 13 A twin sockets outlet | No | 1 |  | 0
Cables, Cable pathways and Conduits
Supply, install, test and commission 450/750 volts 6491X cables with all required accessories for proper installation and operation including conduits, pipes( each cable in separate conduit or pipe), cable lugs, ties... etc. as shown on drawing, as per the preamble, the specifications and supervision engineer's requirements.
6.7.6 | Supply, install and connect complete 1.5 sq. mm colour-coded SC cables to lighting points drawn in Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | M | 10 |  | 0
6.7.7 | Supply and install two compartment floor recessed metallic electrical
floor box with flap cover complete with lifting handle, cable cable flaps,
| as Crabtree Britmac or equal and approved | No. | 1
| PAGE TOTAL CARRIED TO SUMMARY | $ |  |  | 0
ITEM | DESCRIPTION | UNIT | QNTY |  | AMT US$
6.8 | TOILET PIT
Excavations including maintaining and supporting sides
and keeping free from water, mud and fallen material
6.81 | Stripping of surface and excavation for latrine pit in soft soil up to depth of | C.M | 14.4 |  | 0
approximately 1.8m; pit dimensions: 2m width x 4m length
6.82 | Excavation for latrine pit in hard rock at a depth approximately starting at 1.8 M | C.M | 15 |  | 0
Reinforced concrete class 25,
6.8.3 | 150mm thick vibrated reinforced concrete for bottom | C.M | 1.2 |  | 0
slab (concrete class 20)
Reinforcement, as described (PROVISIONAL)
High yield square twisted reinforcement to BS 4461
6.8.4 | 10mm high tensile square twisted bars; cold worked; BS4461 including bends, hooks, tying wire, distance blocks and spacers for bottom slab; Y10@ 200mm c/c . | KG | 130 |  | 0
6.8.5 | Supply and fix sawn formwork to sides of bottom slab | L.M | 12.5 |  | 0
200x400mm block walling bedded and jointed in
cement and sand (1:4) mortar, reinforcement with and
including 25mm wide x 20 gauge hoop iron at every
alternate course as described in:
6.8.6 | Sub-Structure walling | S.M | 22 |  | 0
Cement and sand (1:3) screeds, backings, beds etc
6.8.7 | 15mm thick two coat cement sand (1:3) plaster trowelled smooth and comprising 12mm backing and 3mm finishing coat for internal walls. | S.M | 22 |  | 0
Reinforced concrete class 25,
6.8.8 | Supply all materials and cast a 125mm thick vibrated reinforced | C.M | 1.2 |  | 0
concrete slab, mix1:2:4 or class 20/20. Top slab dimensions 2.5m x 5.0m
| Page Total Carried to Next Page |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QNTY |  | AMT US$
| Page Total Carried Forward from previous Page |  |  |  | 0
Reinforcement, as described (PROVISIONAL)
High yield square twisted reinforcement to BS 4461
6.8.9 | 10mm high tensile square twisted bars; cold worked; BS4461 | KG | 65 |  | 0
including bends, hooks, tying wire, distance blocks and spacers for
top slab; Y10@ 200mm c/c .
6.8.10 | Supply and fix sawn formwork to sides of bottom slab | L.M | 12.5 |  | 0
6.8.11 | Supply and fix sawn formwork beneath the slab | S.M | 12.5 |  | 0
6.8.12 | Manhole frame and covers | Pcs. | 1 |  | 0
6.8.13 | Tank piping, fittings and accessories which includes among others ring bearers anchored in the wall and a 2.5 m heigh 4'' vent pipe with rain cower and fly net | Item | 1 |  | 0
6.8.14 | 4" brown sewer pipes with accessories laid with 1% slope in trench of 0.5 to 0.8 m depth | L.M | 12 |  | 0
Reinforced concrete class 25,
6.8.15 | Supply all materials and cast R.C. buffer beam, 100mm wide x 450mm deep, concrete class 20 | C.M | 0.3 |  | 0
6.8.16 | 12mm high tensile square twisted bars; cold worked; BS4461 including bends, hooks, tying wire, distance blocks and spacers for ring beam reinforcement, 4Y12 | KG | 22 |  | 0

## Grand summary
ITEM NO. | DESCRIPTION | PAGE
GRAND SUMMARY
SECTION NO. 1 | PRELIMINARIES AND GENERAL DESCRIPTIONS
SECTION NO. 2 | SECTION 2: FLAT PACK MODULES
SECTION NO. 3 | SECTION 3: KITCHEN
SECTION NO. 4 | SECTION 4: SECURITY OFFICE
SECTION NO. 5 | SECTION 5: MAIN TOILET
SECTION NO. 6 | SECTION 6: SECURITY TOILET
SECTION NO. 7 | SECTION 7: SECURITY FENCES
SECTION NO. 8 | SECTION 8: WATCH TOWERS
SECTION NO. 9 | SECTION 9 : GATES
SECTION NO. 10 | SECTION 10: SEPTIC TANK
SECTION NO. 11 | SECTION 11: GENERATOR HOUSE
SECTION NO. 12 | SECTION 12: WATER TOWER
SECTION NO. 13 | SECTION 13: SOLAR STREETLIGHTS
SECTION NO. 14 | SECTION 14 : CHILDREN PLAY AREA
SECTION NO. 15 | SECTION 15: STAFF TOILET
TOTAL AMOUNT CARRIED TO FORM OF TENDER
SIGNED:
(CONTRACTOR)
Address:
Tel No:
Date:
SIGNED:
(EMPLOYER )
Address:
Tel No:
Date:

## Sheet5
ITEM | DESCRIPTION | UNIT | QTY | TOTAL
2.8 | ELEMENT NO. 8 : PLUMBING INSTALLATIONS
PIPING
Supply, deliver and install pipes, tubing and fittings as described and shown on the drawings. The pipes shall be PPR PN 20 pipes and all conforming to the current European standards for PPR installations and
to the Engineers approval, pipe jointing shall be by polyfusion or use of
electric coupling and to manufacturer's printed instructions. Rates must
allow for all Metal/plastic threaded adaptors where required, valves,
unions, sockets, sliding and fixed joints, support raceways, isolating
sheaths, elastic material, expansion arms and bends, crossovers, couplings,
clippings, connectors, joints and for the connection of sanitary fixtures etc.
as required in the running lengths of pipework and also where necessary,
for pipe fixing clips, holder bats plugged and screwed for the proper and
satisfactory functioning of the system. The pipes will be pressure tested
before the plastering of wall commences and as per the manufacturers
recommended testing procedures. The sizes indicated are the minimum
bore sizes.
2.8.1 | Supply and install heavy duty PPR pipes including all connections | LS | 1 | 0
SANITARY INSTALLATIONS
Sanitary appliances complete with all the connections to services,
waste, jointing to supply overflows and plugging and scewing
to the floors. Where trade names are mentioned below, the
reference is intended to be as a guide to the type of fitting.
2.8.2 | Pedestal wash hand basin in white vitreous china size 500x400 mm complete with 'Aztec' chromed taps and handles, a 32mm diameter chrome plated pop-up waste and a 32mm Caradon Terrain' plastic bottle trap. Wash hand basin to be as 'Twyford Galerie Design' or equal and approved | No. | 2 | 0
| Page Total Carried Forward |  |  | 0
ITEM | DESCRIPTION | UNIT | QTY | TOTAL
| Page Total brought Forward |  |  | 0
Water closet (W.C.) suite in white vitreous china comprising:
Glazed W.C. pan with heavy duty unbreakable plastic seat and cover,
close couple cistern and fittings, 6.0 litres, including chrome lever and
cover clip and WC outlet connector. The cistern to have internal overflow.
2.8.3 | Water closet pan to be as 'Twyford classic' or equal and approved | No. | 4 | 0
Recessed toilet roll holder in white vitreous china size 150x150 mm.
2.8.4 | To be as 'Twyford' or equal and approved | No. | 4 | 0
Wall-mounted push-button soap dispenser complete with initial charge
and mounting brackets. Soap dispenser to be as 'Star mix' or equal
2.8.5 | and approved | No. | 2 | 0
6 mm thick polished beveled plate glass mirror size 610x610 mm on
foam and 6 mm plywood timber backing in hard wood timber framing
2.8.6 | fixed on wall with dome headed brass screws | No. | 2 | 0
Allow for all all connections, pressure testing at 4 bars for 24hours and
commissioning of the sanitary fittings and accessories to the entire
2.8.7 | satisfaction of the Engineer. | LS | 1 | 0
0
| PLUMBING TOTAL CARRIED TO MAIN SUMMARY |  |  | 0
0
| Total carried to summary | $ |  | 0
MAIN SUMMARY
TOTAL FOR DINING
TOTAL FOR KITCHEN
TOTAL FOR ELECTRICAL WORKS
TOTAL FOR MECHANICAL WORKS
TOTAL FOR SECTION 5: CARRIED TO GRAND SUMMARY